## January 07
BRUNSWICK SEWER DISTRICT | [11 empty] | State Discharge License Number W 002600-5L-C-R | [9 empty] | Certifying Official: |  |  | Francis E. McVey | BRUNSWICK SEWER DISTRICT | [13 empty] | State Discharge License Number W 002600-5L-C-R | [11 empty] | BRUNSWICK SEWER DISTRICT | [9 empty] | State Discharge License Number W 002600-5L-C-R
Monthly Report of Treatment Operations : |  |  |  |  | January | 2007 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [12 empty] | General Manager | Monthly Report of Treatment Operations : |  |  |  |  | January | 2007 | [7 empty] | N.P.D.E.S. Permit Number ME 0100102 | [9 empty] | Page 2. |  | Monthly Report of Treatment Operations : |  |  | January | 2007 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [7 empty] | Page 3.
SETTLEABLE
| FLOW | [6 empty] | WEATHER |  |  |  |  | DISINFECTION |  |  | P.H. |  |  | TEMPERATURE |  |  |  | SOLIDS |  |  |  | BIOCHEMICAL OXYGEN DEMAND | [6 empty] | TOTAL SUSPENDED SOLIDS | [6 empty] | SLUDGE DEWATERING | [7 empty] | SLUDGE UTILIZATION |  |  |  | SUMMARY DATA | [11 empty] | HIGH WEEKLY AVERAGE VALUES
|  | Total | Maxim. | Minim. | [8 empty] | Hypo - | [37 empty] | Stored |  |  |  | LOADING |  |  | CONCENTRATION |  |  |  | REPORTING |  |  |  | BOD |  | TSS |  |  | SETTLEABLE SOLIDS
| Totalizer | Flow | Flow | Flow | Flow | Holding | Septic |  | Average | Total | Grit |  | chlorite | Chlorine | [18 empty] | CBOD | [7 empty] | Quantity | Feed | Filter |  | Cake | Sludge | Lime | Average | Quantity |  | or |  |  |  | Monthly | Daily |  | Mo Aver | High Wkly | Daily |  |  |  | Sample
Date | Reading | Treated | (instant.) | (instant.) | By-passed | Received | Added | Conditions | Temp. | Precip. | Removed |  | Used | Residual | E. Coli | Influent | Primary | Effluent | Influent | Primary | Effluent |  | Influent | Primary | Effluent | Date | Influent | Influent | Primary | Primary | Effluent | Effluent | Effluent | Influent | Influent | Primary | Primary | Effluent | Effluent |  | Dewatered | Solids | Operation | Polymer | Dry Solid | Dewatered | Added | pH | Utilized | Site | Spread |  |  |  | Average | Maximum | Units | Minimum | Average | Maximum | Units | Exceptions | Frequency | Type |  | High Weekly Average |  | High Weekly Average |  |  | High Weekly Average
|  | (MG) | (MG) | (MG) | (MG) | (gallons) | (gallons) |  | (deg. F.) | (inches) | (cu. yd.) |  | (gallons) | (mg/L) | (#/100) | (s.u.) | (s.u.) | (s.u.) | (deg. C.) | (deg. C.) | (deg. C.) |  | (ml/L) | (ml/L) | (ml/L) |  | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) |  | (gallons) | (%) | (hours) | (lbs) | (%) | (cu. yd.) | (lbs) | (s.u.) | (cu. yd.) | [16 empty] | (mg / L) | (lbs / day) | (mg / L) | (lbs / day) |  | (mg / L)
5714152
1 | 5716859 | 2.707 | 4.6 | 1.2 | 0.00 | 0 | 0 | LT RAIN | 31.6 | 0.66 | [5 empty] | 6.81 | 7.02 | 6.85 | 12.4 | 11.2 | 10.8 |  | 1.5 | 0.01 | 0 | 1 | [26 empty] | BOD, 5-day | Reporting : | 329.3235 | 432.8794 | (lbs / day) | 13.4615 | 14.6667 | 16 | (mg / L) | 0 | 03/07 | 24 | Week 1 | 14.6667 | 389.2278 | 20.3333 | 540.621 |  | 0 | check formulas for designation of weeks
2 | 5719931 | 3.072 | 4.5 | 1.3 | 0.00 | 1350 | 7500 | CLEAR | 34.8 | 0.02 | [5 empty] | 7.24 | 7 | 6.92 | 12.5 | 11.4 | 11.4 |  | 10 | 0.01 | 0 | 2 | [26 empty] | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24
3 | 5722993 | 3.062 | 5.6 | 1 | 0.00 | 750 | 2000 | CLEAR | 36 | 0 |  |  | O | O | O | 7.04 | 6.99 | 6.76 | 12.2 | 11.2 | 10.9 |  | 5.5 | 0.3 | 0 | 3 | 233 | 5950.1396 |  |  | 13 | 331.982 | 11 | 248 | 6333.1958 |  |  | 16 | 408.5933 |  | 78108 | 2 | 5 | 37.2 | 31 | 24 | 2100 | 12.32 | 24 | EGYPT | STORED | [13 empty] | Week 2 | 12.3333 | 336.7636 | 16.6667 | 454.3938 |  | 0 | identifies cell for keyed data entry
4 | 5726237 | 3.244 | 5.6 | 1 | 0.00 | 200 | 5750 | CLEAR | 37.1 | 0 | [5 empty] | 7.08 | 7.06 | 6.98 | 11.6 | 11.6 | 11.7 |  | 5.5 | 0.01 | 0 | 4 | 199 | 5383.937 |  |  | 16 | 432.8794 | 13 | 230 | 6222.6408 |  |  | 24 | 649.319
5 | 5729457 | 3.22 | 5.4 | 1.1 | 0.00 | 0 | 7500 | RAIN | 44.5 | 0.01 |  |  | F | F | F | 7.09 | 7 | 6.71 | 12.4 | 11.8 | 12.1 |  | 3.5 | 0 | 0 | 5 | 222 | 5961.7656 | 130 | 3491.124 | 15 | 402.822 | 12 | 210 | 5639.508 | 72 | 1933.5456 | 21 | 563.9508 | [25 empty] | Week 3 | 13.3333 | 310.9986 | 17.6667 | 411.832 |  | 0.0028571
6 | 5732526 | 3.069 | 4.6 | 1 | 0.00 | 0 | 0 | CLOUDY | 53.2 | 0.33 | [5 empty] | 6.86 | 6.93 | 6.39 | 12 | 11.9 | 12.6 |  | 3 | 0.01 | 0 | 6 | [26 empty] | pH | Reporting : | - | - | - | 6.39 | - | 7.15 | (s.u.) | 0 | 01/01 | GR
7 | 5735507 | 2.981 | 4.5 | 1 | 0.00 | 0 | 0 | CLEAR | 42.2 | 0 |  |  | F | F | F | 6.88 | 6.99 | 6.58 | 11.9 | 11.4 | 11.5 |  | 2 | 0.01 | 0 | 7 | [26 empty] | Effluent | Permit : | - | - | - | 6 | - | 8.5 | (s.u.) | - | 01/01 | GR | Week 4 | 13.3333 | 293.2455 | 19.3333 | 424.8924 |  | 0
8 | 5738395 | 2.888 | 5 | 1.5 | 0.00 | 2000 | 2000 | RAIN | 39.5 | 0.91 | [5 empty] | 6.88 | 6.89 | 6.81 | 12.2 | 11.6 | 11.8 |  | 7.5 | 0.01 | 0 | 8 | [14 empty] | 37646 | 4 | 3.25 | 21.7 | 32 | 24 | 1365 | 12.34 | 24 | EGYPT | STORED
9 | 5741978 | 3.583 | 4.6 | 1.4 | 0.00 | 700 | 5000 | CLEAR | 35.6 | 0 | [5 empty] | 7.25 | 7.01 | 6.96 | 12.4 | 11.4 | 11.1 |  | 6 | 0.01 | 0 | 9 | [38 empty] | Week 5
10 | 5745372 | 3.394 | 5.4 | 1.4 | 0.00 | 2200 | 4750 | CLEAR | 26.1 | 0 | [5 empty] | 7.18 | 7.04 | 7.02 | 12.1 | 11.2 | 11.3 |  | 6.5 | 0.01 | 0 | 10 | 182 | 5151.6847 |  |  | 12 | 339.6715 | 10 | 180 | 5095.0728 |  |  | 14 | 396.2834
11 | 5748733 | 3.361 | 4.4 | 1.1 | 0.00 | 0 | 3000 | CLEAR | 20.7 | 0 |  |  | F | F | F | 6.94 | 6.99 | 6.8 | 11.7 | 9.3 | 9 |  | 2 | 0.01 | 0 | 11 | 194 | 5437.9636 |  |  | 10 | 280.3074 | 9 | 174 | 4877.3488 |  |  | 15 | 420.4611 |  | 33335 | 3 | 3.5 | 21.7 | 31 | 24 | 1680 | 12.35 | 24 | EGYPT | STORED |  | TSS | Reporting : | 461.0166 | 649.319 | (lbs / day) | 18.9231 | 20.3333 | 24 | (mg / L) | 0 | 03/07 | 24
12 | 5751853 | 3.12 | 4.6 | 1.1 | 0.00 | 6500 | 2750 | CLOUDY | 36.7 | 0 | [5 empty] | 7.08 | 6.97 | 7.03 | 12.3 | 11.4 | 10.9 |  | 5.5 | 0.1 | 0 | 12 | 177 | 4605.6816 | 101 | 2628.1008 | 15 | 390.312 | 12 | 174 | 4527.6192 | 59 | 1535.2272 | 21 | 546.4368 | [13 empty] | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24 | Maximum | 14.6667 | 389.2278 | 20.3333 | 540.621 |  | 0.0028571
13 | 5754910 | 3.057 | 4.6 | 1.1 | 0.00 | 0 | 0 | CLOUDY | 37.6 | 0.01 |  |  | O | O | O | 6.79 | 6.87 | 6.82 | 11.8 | 11.4 | 11.7 |  | 2.5 | 0.1 | 0 | 13
14 | 5757823 | 2.913 | 4.2 | 1 | 0.00 | 0 | 1500 | SNOW | 24.4 | 0 | [5 empty] | 6.84 | 6.94 | 6.9 | 11.6 | 10.9 | 10.8 |  | 2.5 | 0.01 | 0.01 | 14
15 | 5760622 | 2.799 | 4.2 | 1 | 0.00 | 0 | 2000 | CLOUDY | 22.1 | 0 |  |  | R | R | R | 6.76 | 6.86 | 6.89 | 11.4 | 10.9 | 10.6 |  | 2 | 0.1 | 0 | 15
16 | 5763550 | 2.928 | 4.2 | 1 | 0.00 | 1550 | 3000 | CLEAR | 18.6 | 0.02 | [5 empty] | 7.2 | 7.03 | 7.11 | 12.2 | 11 | 10.1 |  | 7 | 0.01 | 0 | 16 | [14 empty] | 40492 | 4 | 3.75 | 24.8 | 33 | 24 | 1687.5 | 12.33 | 24 | EGYPT | STORED |  | SETTLEABLE
17 | 5766387 | 2.837 | 4.2 | 1 | 0.00 | 0 | 0 | CLEAR | 4.7 | 0 | [5 empty] | 6.98 | 6.95 | 7.04 | 12.2 | 10.5 | 9.8 |  | 3.5 | 0.01 | 0 | 17 | 225 | 5323.6305 |  |  | 12 | 283.927 | 11 | 188 | 4448.189 |  |  | 16 | 378.5693 | [13 empty] | SOLIDS | Reporting : | - | - | - | - | 0.0028571 | 0.01 | (mg / L) | 0 | 01/01 | GR
18 | 5769185 | 2.798 | 4.8 | 1 | 0.00 | 200 | 0 | CLEAR | 16 | 0.03 | [5 empty] | 7.21 | 6.99 | 6.88 | 12.2 | 10.7 | 8.8 |  | 6 | 0.1 | 0 | 18 | 216 | 5040.4291 |  |  | 14 | 326.6945 | 12 | 246 | 5740.4887 |  |  | 16 | 373.3651 |  | 21806 | 3 | 1.5 | 12.4 | 33 | 12 | 675 | 12.45 | 12 | EGYPT | STORED |  | Effluent | Permit : | - | - | - | - | (Report) | 0.3 | (mg / L) | - | 01/01 | GR
19 | 5771946 | 2.761 | 4 | 1 | 0.00 | 0 | 4750 | SNOW | 30.5 | 0.06 |  |  | S | S | S | 6.98 | 7.01 | 6.78 | 11.5 | 10.8 | 10.6 |  | 6.5 | 0.01 | 0.01 | 19 | 199 | 4582.3213 | 126 | 2901.3692 | 14 | 322.3744 | 12 | 167 | 3845.4656 | 61 | 1404.6311 | 21 | 483.5615
20 | 5774613 | 2.667 | 4.4 | 1.2 | 0.00 | 0 | 0 | CLOUDY | 21.8 | 0 | [5 empty] | 6.93 | 7.07 | 6.65 | 11.6 | 8.7 | 9 |  | 2.5 | 0.1 | 0 | 20
21 | 5777326 | 2.713 | 4.2 | 1.2 | 0.00 | 0 | 0 | CLOUDY | 13.8 | 0 |  |  | E | E | E | 6.92 | 7.01 | 6.82 | 11.7 | 7.4 | 6.9 |  | 4 | 0.01 | 0 | 21
22 | 5780047 | 2.721 | 4.2 | 1.2 | 0.00 | 200 | 2000 | CLEAR | 17.5 | 0.05 | [5 empty] | 6.81 | 6.99 | 6.81 | 11.7 | 10.4 | 9.6 |  | 5 | 0.01 | 0 | 22 | [14 empty] | 63166 | 2 | 5 | 34.1 | 31 | 24 | 2100 | 12.32 | 24 | EGYPT | STORED |  | FLOW | Reporting : | 2.8803 | 3.583 | (MGD) | - | - | - | - | 0 | 99/99 | RC |  |  |  | CBOD
23 | 5782800 | 2.753 | 4 | 1.1 | 0.00 | 0 | 0 | LT SNOW | 22.5 | 0.09 |  |  | A | A | A | 7.19 | 7.02 | 6.87 | 11.3 | 10.9 | 10 |  | 4 | 0.01 | 0 | 23 | [26 empty] | Effluent | Permit : | 3.85 | (Report) | (MGD) | - | - | - | - | - | 99/99 | RC
24 | 5785389 | 2.589 | 4.1 | 1.1 | 0.00 | 2800 | 5000 | CLEAR | 24.4 | 0.17 | [5 empty] | 7.44 | 7.06 | 6.86 | 12.1 | 11.5 | 11.1 |  | 7.5 | 0.01 | 0 | 24 | 220 | 4750.2972 |  |  | 14 | 302.2916 | 12 | 208 | 4491.1901 |  |  | 20 | 431.8452 | [28 empty] | % Removal
25 | 5788031 | 2.642 | 4.4 | 1.2 | 0.00 | 1500 | 3250 | CLEAR | 11.1 | 0 |  |  | S | S | S | 7.2 | 7 | 7.15 | 11.6 | 10.9 | 10.3 |  | 4.5 | 0.01 | 0 | 25 | 255 | 5618.7414 |  |  | 12 | 264.4114 | 10 | 206 | 4539.0617 |  |  | 21 | 462.7199 |  | 23808 | 3 | 2.25 | 15.5 | 32 | 12 | 1147.5 | 12.47 | 12 | EGYPT | STORED
26 | 5790712 | 2.681 | 4.1 | 1 | 0.00 | 1200 | 3000 | CLEAR | 1.1 | 0 | [5 empty] | 7.09 | 7.12 | 7.02 | 11.6 | 8.6 | 8.5 |  | 5 | 0.01 | 0 | 26 | 230 | 5142.6942 | 154 | 3443.3692 | 14 | 313.0336 | 12 | 256 | 5724.0422 | 81 | 1811.1227 | 17 | 380.1122 | [28 empty] | 94.7881
27 | 5793303 | 2.591 | 4.2 | 1 | 0.00 | 0 | 0 | CLOUDY | 7.6 | 0 |  |  | O | O | O | 7.1 | 7.18 | 6.8 | 11.3 | 9.3 | 8.1 |  | 4.5 | 0.01 | 0 | 27 | [26 empty] | BOD, 5-day | Reporting : | - | - | - | 93.7282 | - | - | (percent) | 0 | 01/30 | CA
28 | 5795824 | 2.521 | 4 | 1 | 0.00 | 0 | 0 | LT SNOW | 18.5 | 0.02 | [5 empty] | 6.98 | 7.12 | 6.9 | 11.7 | 10.1 | 9.6 |  | 1.5 | 0.01 | 0 | 28 | [26 empty] | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
29 | 5798411 | 2.587 | 4.2 | 1 | 0.00 | 1200 | 3000 | CLEAR | 16.2 | 0 |  |  | N | N | N | 7.12 | 7.08 | 7.03 | 11.9 | 10.4 | 9.8 |  | 5.5 | 0.01 | 0 | 29 | [14 empty] | 43565 | 3 | 3.75 | 24.8 | 31 | 24 | 1800 | 12.39 | 24 | EGYPT | STORED
30 | 5800952 | 2.541 | 4 | 1 | 0.00 | 3500 | 2000 | CLEAR | 7.3 | 0 | [5 empty] | 7.29 | 7.18 | 7.13 | 11.9 | 10 | 9.7 |  | 6.5 | 0.01 | 0 | 30
31 | 5803440 | 2.488 | 4 | 1 | 0.00 | 5000 | 2750 | CLOUDY | 17.3 | 0.01 | [5 empty] | 7.14 | 7.15 | 6.82 | 12.1 | 10.7 | 10 |  | 7.5 | 0.01 | 0 | 31 | 256 | 5311.9795 |  |  | 14 | 290.4989 | 12 | 256 | 5311.9795 |  |  | 24 | 497.9981
[53 empty] | TSS | Reporting : | - | - | - | 91.0317 | - | - | (percent) | 0 | 01/30 | CA
Total | 89288 | 89.288 | - | - | 0 | 30850 | 72500 | - | - | 2.39 | 0.0 |  | 0 | - | - | - | - | - | - | - | - |  | - | - | - | Total | - | - | - | - | - | - | - | - | - | - | - | - | - |  | 341926 | - | 28 | 192.2 | - | 168 | 12555 | - | 168 | - | - |  | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
Maximum | - | 3.583 | 5.6 | 1.5 | 0 | 6500 | 7500 | - | 53.2 | 0.91 | - |  | - | - | - | 7.44 | 7.18 | 7.15 | 12.5 | 11.9 | 12.6 |  | 10 | 0.3 | 0.01 | Maximum | 256 | 5961.7656 | 154 | 3491.124 | 16 | 432.8794 | 13 | 256 | 6333.1958 | 81 | 1933.5456 | 24 | 649.319 |  | - | 4 | - | - | 33 | - | - | 12.47 | - | - | -
Minimum | - | 2.488 | 4 | 1 | 0 | 0 | 0 | - | 1.1 | 0 | - |  | - | - | - | 6.76 | 6.86 | 6.39 | 11.3 | 7.4 | 6.9 |  | 1.5 | 0 | 0 | Minimum | 177 | 4582.3213 | 101 | 2628.1008 | 10 | 264.4114 | 9 | 167 | 3845.4656 | 59 | 1404.6311 | 14 | 373.3651 |  | - | 2 | - | - | 31 | - | - | 12.32 | - | - | -
Average | - | 2.8803 | 4.4774 | 1.1032 | 0.000 | 995.1613 | 2338.7097 | - | 24.871 | 0.077097 | - |  | - | - | - | 7.0419 | 7.0168 | 6.8739 | 11.9065 | 10.6613 | 10.3258 |  | 4.7258 | 0.033548 | 0.00064516 | Average | 216 | 5250.8666 | 127.75 | 3115.9908 | 13.4615 | 329.3235 | 11.3846 | 211 | 5138.1386 | 68.25 | 1671.1317 | 18.9231 | 461.0166 |  | 42740.75 | 3 | 3.5 | 24.025 | 31.75 | 21 | 1569.375 | 12.3712 | 21 | - | -
[13 empty] | Geometric Mean : |  | - | [14 empty] | Percent Removal : |  | 93.7282 |  |  |  | Percent Removal : |  | 91.0317

## Graph Jan07
Plant Capacity
3.85 mgd

## February 07
BRUNSWICK SEWER DISTRICT | [11 empty] | State Discharge License Number W 002600-5L-C-R | [9 empty] | Certifying Official: |  |  | Francis E. McVey | BRUNSWICK SEWER DISTRICT | [14 empty] | State Discharge License Number W 002600-5L-C-R | [11 empty] | BRUNSWICK SEWER DISTRICT | [9 empty] | State Discharge License Number W 002600-5L-C-R
Monthly Report of Treatment Operations : |  |  |  |  | February | 2007 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [12 empty] | General Manager | Monthly Report of Treatment Operations : | [5 empty] | February | 2007 | [7 empty] | N.P.D.E.S. Permit Number ME 0100102 | [9 empty] | Page 2. |  | Monthly Report of Treatment Operations : |  |  | February | 2007 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [7 empty] | Page 3.
SETTLEABLE
| FLOW | [6 empty] | WEATHER |  |  |  |  | DISINFECTION |  |  | P.H. |  |  | TEMPERATURE |  |  |  | SOLIDS |  |  |  |  | BIOCHEMICAL OXYGEN DEMAND | [6 empty] | TOTAL SUSPENDED SOLIDS | [6 empty] | SLUDGE DEWATERING | [7 empty] | SLUDGE UTILIZATION |  |  |  | SUMMARY DATA | [11 empty] | HIGH WEEKLY AVERAGE VALUES
|  | Total | Maxim. | Minim. | [8 empty] | Hypo - | [38 empty] | Stored |  |  |  | LOADING |  |  | CONCENTRATION |  |  |  | REPORTING |  |  |  | BOD |  | TSS |  |  | SETTLEABLE SOLIDS
| Totalizer | Flow | Flow | Flow | Flow | Holding | Septic |  | Average | Total | Grit |  | chlorite | Chlorine | [19 empty] | CBOD | [7 empty] | Quantity | Feed | Filter |  | Cake | Sludge | Lime | Average | Quantity |  | or |  |  |  | Monthly | Daily |  | Mo Aver | High Wkly | Daily |  |  |  | Sample
Date | Reading | Treated | (instant.) | (instant.) | By-passed | Received | Added | Conditions | Temp. | Precip. | Removed |  | Used | Residual | E. Coli | Influent | Primary | Effluent | Influent | Primary | Effluent |  | Influent | Primary | Effluent | Date |  | Influent | Influent | Primary | Primary | Effluent | Effluent | Effluent | Influent | Influent | Primary | Primary | Effluent | Effluent |  | Dewatered | Solids | Operation | Polymer | Dry Solid | Dewatered | Added | pH | Utilized | Site | Spread |  |  |  | Average | Maximum | Units | Minimum | Average | Maximum | Units | Exceptions | Frequency | Type |  | High Weekly Average |  | High Weekly Average |  |  | High Weekly Average
|  | (MG) | (MG) | (MG) | (MG) | (gallons) | (gallons) |  | (deg. F.) | (inches) | (cu. yd.) |  | (gallons) | (mg/L) | (#/100) | (s.u.) | (s.u.) | (s.u.) | (deg. C.) | (deg. C.) | (deg. C.) |  | (ml/L) | (ml/L) | (ml/L) |  |  | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) |  | (gallons) | (%) | (hours) | (lbs) | (%) | (cu. yd.) | (lbs) | (s.u.) | (cu. yd.) | [16 empty] | (mg / L) | (lbs / day) | (mg / L) | (lbs / day) |  | (mg / L)
5803440
1 | 5805893 | 2.453 | 4.4 | 1 | 0.00 | 1300 | 1750 | CLOUDY | 27 | 0.01 | [5 empty] | 7.27 | 7.14 | 6.6 | 12 | 11 | 10.4 |  | 13 | 0.01 | 0 | 1 |  | 258 | 5278.1692 |  |  | 15 | 306.8703 | 13 | 330 | 6751.1466 |  |  | 22 | 450.0764 |  | 25906 | 4 | 1.75 | 15.5 | 32 | 12 | 892.5 | 12.46 | 12 | EGYPT | STORE |  | BOD, 5-day | Reporting : | 284.7102 | 374.0156 | (lbs / day) | 14.4167 | 15.6667 | 17 | (mg / L) | 0 | 03/07 | 24 | Week 1 | 14 | 309 | 24 | 495 |  | 0 | check formulas for designation of weeks
2 | 5808370 | 2.477 | 3.8 | 0.8 | 0.00 | 200 | 0 | CLOUDY | 23.8 | 0 | [5 empty] | 7.19 | 7.12 | 6.69 | 11.9 | 10.7 | 10.3 |  | 6.5 | 0.01 | 0 | 2 |  | 297 | 6135.4795 | 168 | 3470.5742 | 16 | 330.5309 | 13 | 208 | 4296.9014 | 66 | 1363.4399 | 26 | 537.1127 | [13 empty] | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24
3 | 5810742 | 2.372 | 4 | 1 | 0.00 | 1000 | 0 | SNOW | 27 | 0.11 |  |  | O | O | O | 7.18 | 7.06 | 6.63 | 11.9 | 10.5 | 9.4 |  | 3.5 | 0.01 | 0 | 3 | [39 empty] | Week 2 | 15.6667 | 322.7691 | 20.6667 | 425.1537 |  | 0.0057143 | identifies cell for keyed data entry
4 | 5813094 | 2.352 | 4 | 0.8 | 0.00 | 0 | 0 | CLOUDY | 17.4 | 0 | [5 empty] | 7.07 | 7.15 | 6.91 | 11.4 | 10.3 | 9.1 |  | 4 | 0.01 | 0 | 4
5 | 5815489 | 2.395 | 3.8 | 0.9 | 0.00 | 1000 | 1000 | CLEAR | 9 | 0 |  |  | F | F | F | 7.13 | 7.18 | 7.19 | 11.8 | 10.6 | 9.2 |  | 4 | 0 | 0 | 5 | [39 empty] | Week 3 | 11.3333 | 209.2812 | 22 | 404.8069 |  | 0
6 | 5817922 | 2.433 | 4.6 | 1 | 0.00 | 3700 | 1000 | CLEAR | 12.9 | 0 | [5 empty] | 7.39 | 7.14 | 6.95 | 11.8 | 10.8 | 8.9 |  | 8 | 0.1 | 0.01 | 6 | [15 empty] | 49544 | 4 | 3.25 | 21.7 | 33 | 24 | 1657.5 | 12.39 | 24 | EGYPT | STORE |  | pH | Reporting : | - | - | - | 6.35 | - | 7.19 | (s.u.) | 0 | 01/01 | GR
7 | 5820560 | 2.638 | 3.8 | 1 | 0.00 | 0 | 1000 | CLEAR | 6.6 | 0 |  |  | F | F | F | 7.35 | 7.18 | 7.02 | 12.8 | 10.7 | 10.3 |  | 8.5 | 0.01 | 0.01 | 7 |  | 218 | 4796.2006 |  |  | 17 | 374.0156 | 14 | 196 | 4312.1803 |  |  | 21 | 462.0193 | [13 empty] | Effluent | Permit : | - | - | - | 6 | - | 8.5 | (s.u.) | - | 01/01 | GR | Week 4 | 15.3333 | 302.8754 | 22.6667 | 445.8481 |  | 0.0042857
8 | 5822963 | 2.403 | 3.8 | 0.9 | 0.00 | 2450 | 2000 | CLEAR | 10 | 0 | [5 empty] | 7.37 | 7.18 | 6.8 | 11.6 | 9.6 | 8.9 |  | 10 | 0.1 | 0.01 | 8 |  | 254 | 5090.4191 |  |  | 14 | 280.5743 | 12 | 312 | 6252.7982 |  |  | 22 | 440.9024 |  | 34614 | 3 | 2.5 | 15.5 | 33 | 18 | 1275 | 12.38 | 18 | EGYPT | STORE
9 | 5825314 | 2.351 | 4.6 | 0.8 | 0.00 | 0 | 3000 | CLEAR | 12.6 | 0 | [5 empty] | 7.17 | 7.18 | 6.67 | 11.7 | 10.2 | 9.1 |  | 7.5 | 0.01 | 0 | 9 |  | 302 | 5921.4167 | 176 | 3450.8918 | 16 | 313.7174 | 13 | 362 | 7097.8571 | 77 | 1509.7652 | 19 | 372.5395 | [25 empty] | Week 5
10 | 5827887 | 2.573 | 4 | 0.8 | 0.00 | 0 | 0 | CLOUDY | 15.5 | 0 | [5 empty] | 7.07 | 7.12 | 6.55 | 11.1 | 10.6 | 9.5 |  | 3 | 0.1 | 0.01 | 10
11 | 5830151 | 2.264 | 4 | 0.8 | 0.00 | 0 | 0 | CLEAR | 18.8 | 0 |  |  | F | F | F | 7.22 | 7.17 | 6.74 | 11 | 10.5 | 9.6 |  | 4 | 0.01 | 0 | 11 | [27 empty] | TSS | Reporting : | 430.1765 | 537.1127 | (lbs / day) | 21.9167 | 24 | 26 | (mg / L) | 0 | 03/07 | 24
12 | 5832432 | 2.281 | 4 | 0.8 | 0.00 | 0 | 3000 | CLEAR | 21.5 | 0.01 | [5 empty] | 7.23 | 7.13 | 6.83 | 12 | 10.2 | 9.7 |  | 6.5 | 0.01 | 0 | 12 | [27 empty] | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24 | Maximum | 15.6667 | 322.7691 | 24 | 495 |  | 0.0057143
13 | 5834699 | 2.267 | 3.8 | 0.8 | 0.00 | 2200 | 1000 | CLEAR | 9.8 | 0 |  |  | O | O | O | 7.17 | 7.21 | 6.7 | 11.3 | 10.2 | 8.8 |  | 9 | 0.1 | 0 | 13 | [15 empty] | 52571 | 3 | 3.5 | 27.9 | 33 | 24 | 1785 | 12.39 | 24 | EGYPT | STORE
14 | 5836985 | 2.286 | 3.8 | 0.8 | 0.00 | 0 | 0 | SNOW | 13.1 | 0 | [5 empty] | 7.21 | 7.17 | 6.8 | 11.1 | 10.8 | 8.9 |  | 3.5 | 0.01 | 0 | 14 |  | 312 | 5948.3549 |  |  | 13 | 247.8481 | 12 | 238 | 4537.5271 |  |  | 22 | 419.4353
15 | 5839118 | 2.133 | 3.6 | 0.8 | 0.00 | 600 | 3000 | CLEAR | 16.1 | 0.08 |  |  | R | R | R | 7.21 | 7.1 | 6.58 | 10.7 | 9.4 | 5.6 |  | 7 | 0.01 | 0 | 15 |  | 242 | 4304.9912 |  |  | 10 | 177.8922 | 9 | 254 | 4518.4619 |  |  | 23 | 409.1521
16 | 5841321 | 2.203 | 3.6 | 0.8 | 0.00 | 0 | 2000 | CLEAR | 15 | 0 | [5 empty] | 7.07 | 7.13 | 6.35 | 10.8 | 9.5 | 8.3 |  | 6 | 0.1 | 0 | 16 |  | 263 | 4832.1043 | 149 | 2737.58 | 11 | 202.1032 | 10 | 254 | 4666.7471 | 75 | 1377.9765 | 21 | 385.8334 |  | 39396 | 3 | 3.25 | 18.6 | 33 | 18 | 1657.5 | 12.36 | 18 | EGYPT | STORE |  | SETTLEABLE
17 | 5843521 | 2.2 | 4 | 0.8 | 0.00 | 4000 | 1000 | CLEAR | 26.8 | 0.27 | [5 empty] | 7.03 | 7.15 | 6.69 | 10.1 | 8.4 | 8.2 |  | 1.5 | 0.1 | 0 | 17 | [27 empty] | SOLIDS | Reporting : | - | - | - | - | 0.0057143 | 0.01 | (mg / L) | 0 | 01/01 | GR
18 | 5845672 | 2.151 | 3.8 | 0.8 | 0.00 | 0 | 0 | CLOUDY | 25.2 | 0.06 | [5 empty] | 7.27 | 7.17 | 6.73 | 10.7 | 9 | 8.7 |  | 4.5 | 0.01 | 0 | 18 | [27 empty] | Effluent | Permit : | - | - | - | - | (Report) | 0.3 | (mg / L) | - | 01/01 | GR
19 | 5847794 | 2.122 | 4 | 0.7 | 0.00 | 0 | 0 | CLEAR | 12.1 | 0 |  |  | S | S | S | 7.31 | 7.23 | 6.67 | 10.6 | 8.7 | 7.6 |  | 5 | 0.1 | 0.01 | 19
20 | 5850012 | 2.218 | 4 | 0.6 | 0.00 | 0 | 5000 | CLEAR | 16.3 | 0 | [5 empty] | 7.07 | 7.18 | 6.62 | 10.2 | 9.7 | 9.2 |  | 6 | 0.1 | 0.01 | 20 | [15 empty] | 29164 | 3 | 2 | 15.5 | 33 | 12 | 1020 | 12.34 | 12 | EGYPT | STORE
21 | 5852226 | 2.214 | 4.7 | 0.6 | 0.00 | 0 | 750 | CLEAR | 28.7 | 0 |  |  | E | E | E | 7.2 | 7.16 | 6.73 | 11.4 | 10.7 | 10.2 |  | 7 | 0.01 | 0.01 | 21 |  | 283 | 5225.5271 |  |  | 14 | 258.5066 | 12 | 314 | 5797.9346 |  |  | 25 | 461.619
22 | 5854941 | 2.715 | 3.8 | 0.6 | 0.00 | 0 | 3000 | CLEAR | 24.8 | 0 | [5 empty] | 7.39 | 7.18 | 6.62 | 10.9 | 10.8 | 10.3 |  | 6 | 0.01 | 0 | 22 |  | 229 | 5185.2699 |  |  | 16 | 362.2896 | 13 | 276 | 6249.4956 |  |  | 22 | 498.1482 | [13 empty] | FLOW | Reporting : | 2.3099 | 2.715 | (MGD) | - | - | - | - | 0 | 99/99 | RC |  |  |  | CBOD
23 | 5857098 | 2.157 | 4.6 | 0.8 | 0.00 | 3000 | 2000 | CLEAR | 24 | 0 |  |  | A | A | A | 7.21 | 7.11 | 6.5 | 11.2 | 11.1 | 9.8 |  | 12 | 0.01 | 0 | 23 |  | 263 | 4731.2069 | 163 | 2932.2689 | 16 | 287.8301 | 13 | 286 | 5144.9627 | 84 | 1511.1079 | 21 | 377.777 |  | 43571 | 4 | 3.25 | 24.8 | 32 | 24 | 1657.5 | 12.32 | 24 | EGYPT | STORE |  | Effluent | Permit : | 3.85 | (Report) | (MGD) | - | - | - | - | - | 99/99 | RC
24 | 5859512 | 2.414 | 4 | 0.6 | 0.00 | 0 | 0 | CLEAR | 21.1 | 0 | [5 empty] | 7.28 | 7.32 | 6.88 | 10.2 | 9.7 | 8.8 |  | 1.4 | 0.01 | 0 | 24 | [42 empty] | % Removal
25 | 5861646 | 2.134 | 4 | 0.6 | 0.00 | 0 | 0 | CLEAR | 29.8 | 0 |  |  | S | S | S | 7.14 | 7.21 | 6.96 | 10.5 | 9.8 | 9.2 |  | 1.5 | 0.01 | 0 | 25
26 | 5863793 | 2.147 | 3.8 | 0.6 | 0.00 | 0 | 2250 | CLOUDY | 27.1 | 0 | [5 empty] | 7.25 | 7.16 | 6.91 | 11.5 | 11.7 | 10.3 |  | 6.5 | 0 | 0 | 26 | [15 empty] | 25726 | 3 | 2 | 9.1 | 33 | 12 | 960 | 12.43 | 12 | EGYPT | STORE | [16 empty] | 95.5613
27 | 5865924 | 2.131 | 4.2 | 0.6 | 0.00 | 3500 | 2500 | CLEAR | 26.5 | 0 |  |  | O | O | O | 7.2 | 7.21 | 6.89 | 10.9 | 9.8 | 10 |  | 10 | 0 | 0 | 27 | [27 empty] | BOD, 5-day | Reporting : | - | - | - | 94.6121 | - | - | (percent) | 0 | 01/30 | CA
28 | 5868117 | 2.193 | 4.2 | 0.6 | 0.00 | 1500 | 1000 | CLEAR | 33.7 | 0 | 5 |  |  |  |  | 7.61 | 7.29 | 6.46 | 11.7 | 11.2 | 10.9 |  | 10 | 0.01 | 0 | 28 | * | 326 | 5962.4161 |  |  | 15 | 274.3443 | 12 | 344 | 6291.6293 |  |  | 19 | 347.5028 | [13 empty] | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
29 | [12 empty] | N | N | N | [10 empty] | 29
30 | [25 empty] | 30
31 | [25 empty] | 31
[54 empty] | TSS | Reporting : | - | - | - | 92.2051 | - | - | (percent) | 0 | 01/30 | CA
Total | 64677 | 64.677 | - | - | 0 | 24450 | 36250 | - | - | 0.54 | 5 |  | 0 | - | - | - | - | - | - | - | - |  | - | - | - | Total |  | - | - | - | - | - | - | - | - | - | - | - | - | - |  | 300492 | - | 21.5 | 148.6 | - | 144 | 10905 | - | 144 | - | - |  | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
Maximum | - | 2.715 | 4.7 | 1 | 0 | 4000 | 5000 | - | 33.7 | 0.27 | - |  | - | - | - | 7.61 | 7.32 | 7.19 | 12.8 | 11.7 | 10.9 |  | 13 | 0.1 | 0.01 | Maximum |  | 326 | 6135.4795 | 176 | 3470.5742 | 17 | 374.0156 | 14 | 362 | 7097.8571 | 84 | 1511.1079 | 26 | 537.1127 |  | - | 4 | - | - | 33 | - | - | 12.46 | - | - | -
Minimum | - | 2.122 | 3.6 | 0.6 | 0 | 0 | 0 | - | 6.6 | 0 | - |  | - | - | - | 7.03 | 7.06 | 6.35 | 10.1 | 8.4 | 5.6 |  | 1.4 | 0 | 0 | Minimum |  | 218 | 4304.9912 | 149 | 2737.58 | 10 | 177.8922 | 9 | 196 | 4296.9014 | 66 | 1363.4399 | 19 | 347.5028 |  | - | 3 | - | - | 32 | - | - | 12.32 | - | - | -
Average | - | 2.3099 | 4.025 | 0.775 | 0.000 | 873.2143 | 1294.6429 | - | 19.7214 | 0.019286 | - |  | - | - | - | 7.2236 | 7.1689 | 6.7382 | 11.2429 | 10.2214 | 9.2571 |  | 6.2643 | 0.034643 | 0.0025 | Average |  | 270.5833 | 5284.2963 | 164 | 3147.8288 | 14.4167 | 284.7102 | 12.1667 | 281.1667 | 5493.1368 | 75.5 | 1440.5724 | 21.9167 | 430.1765 |  | 37561.5 | 3.375 | 2.6875 | 18.575 | 32.75 | 18 | 1363.125 | 12.3837 | 18 | - | -
[13 empty] | Geometric Mean : |  | - | [15 empty] | Percent Removal : |  | 94.6121 |  |  |  | Percent Removal : |  | 92.2051
[27 empty] | * | Eff not a 24 hr composite, sampler problems

## Graph Feb07
Plant Capacity
3.85 mgd

## March 07
BRUNSWICK SEWER DISTRICT | [11 empty] | State Discharge License Number W 002600-5L-C-R | [9 empty] | Certifying Official: |  |  | Francis E. McVey | BRUNSWICK SEWER DISTRICT | [13 empty] | State Discharge License Number W 002600-5L-C-R | [11 empty] | BRUNSWICK SEWER DISTRICT | [9 empty] | State Discharge License Number W 002600-5L-C-R
Monthly Report of Treatment Operations : |  |  |  |  | March | 2007 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [12 empty] | General Manager | Monthly Report of Treatment Operations : |  |  |  |  | March | 2007 | [7 empty] | N.P.D.E.S. Permit Number ME 0100102 | [9 empty] | Page 2. |  | Monthly Report of Treatment Operations : |  |  | March | 2007 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [7 empty] | Page 3.
SETTLEABLE
| FLOW | [6 empty] | WEATHER |  |  |  |  | DISINFECTION |  |  | P.H. |  |  | TEMPERATURE |  |  |  | SOLIDS |  |  |  | BIOCHEMICAL OXYGEN DEMAND | [6 empty] | TOTAL SUSPENDED SOLIDS | [6 empty] | SLUDGE DEWATERING | [7 empty] | SLUDGE UTILIZATION |  |  |  | SUMMARY DATA | [11 empty] | HIGH WEEKLY AVERAGE VALUES
|  | Total | Maxim. | Minim. | [8 empty] | Hypo - | [37 empty] | Stored |  |  |  | LOADING |  |  | CONCENTRATION |  |  |  | REPORTING |  |  |  | BOD |  | TSS |  |  | SETTLEABLE SOLIDS
| Totalizer | Flow | Flow | Flow | Flow | Holding | Septic |  | Average | Total | Grit |  | chlorite | Chlorine | [18 empty] | CBOD | [7 empty] | Quantity | Feed | Filter |  | Cake | Sludge | Lime | Average | Quantity |  | or |  |  |  | Monthly | Daily |  | Mo Aver | High Wkly | Daily |  |  |  | Sample
Date | Reading | Treated | (instant.) | (instant.) | By-passed | Received | Added | Conditions | Temp. | Precip. | Removed |  | Used | Residual | E. Coli | Influent | Primary | Effluent | Influent | Primary | Effluent |  | Influent | Primary | Effluent | Date | Influent | Influent | Primary | Primary | Effluent | Effluent | Effluent | Influent | Influent | Primary | Primary | Effluent | Effluent |  | Dewatered | Solids | Operation | Polymer | Dry Solid | Dewatered | Added | pH | Utilized | Site | Spread |  |  |  | Average | Maximum | Units | Minimum | Average | Maximum | Units | Exceptions | Frequency | Type |  | High Weekly Average |  | High Weekly Average |  |  | High Weekly Average
|  | (MG) | (MG) | (MG) | (MG) | (gallons) | (gallons) |  | (deg. F.) | (inches) | (cu. yd.) |  | (gallons) | (mg/L) | (#/100) | (s.u.) | (s.u.) | (s.u.) | (deg. C.) | (deg. C.) | (deg. C.) |  | (ml/L) | (ml/L) | (ml/L) |  | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) |  | (gallons) | (%) | (hours) | (lbs) | (%) | (cu. yd.) | (lbs) | (s.u.) | (cu. yd.) | [16 empty] | (mg / L) | (lbs / day) | (mg / L) | (lbs / day) |  | (mg / L)
5868117
1 | 5870310 | 2.193 | 4.4 | 0.6 | 0.00 | 0 | 8500 | CLEAR | 28.2 | 0 | [5 empty] | 7.4 | 7.22 | 6.04 | 11.4 | 11.4 | 11.2 |  | 8 | 0.01 | 0 | 1 | 298 | 5450.3068 |  |  | 16 | 292.6339 | 13 | 218 | 3987.1372 |  |  | 27 | 493.8197 |  | 40433 | 4 | 2.75 | 21.7 | 33 | 24 | 1237.5 | 12.38 | 24 | EGYPT | STORE |  | BOD, 5-day | Reporting : | 330.9241 | 579.1796 | (lbs / day) | 15.3571 | 20 | 26 | (mg / L) | 0 | 03/07 | 24 | Week 1 | 16 | 296 | 24 | 429 |  | 0 | check formulas for designation of weeks
2 | 5872448 | 2.138 | 3.6 | 0.6 | 0.00 | 0 | 0 | SNOW | 30.9 | 0.48 | [5 empty] | 7.03 | 7.17 | 6.45 | 11.5 | 10.7 | 10.3 |  | 8.5 | 0.01 | 0 | 2 | 312 | 5563.247 | 193 | 3441.3676 | 18 | 320.9566 | 15 | 278 | 4956.9958 | 93 | 1658.2756 | 25 | 445.773 | [13 empty] | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24
3 | 5874547 | 2.099 | 4 | 0.6 | 0.00 | 0 | 2500 | CLEAR | 33.5 | 0.43 |  |  | O | O | O | 7.07 | 7.18 | 6.42 | 11.5 | 10.2 | 10 |  | 4.5 | 0.01 | 0 | 3 | [38 empty] | Week 2 | 14.6667 | 252.007 | 17 | 292.0334 |  | 0.0042857 | identifies cell for keyed data entry
4 | 5876687 | 2.14 | 3.8 | 0.6 | 0.00 | 0 | 0 | CLEAR | 33.9 | 0.02 | [5 empty] | 7 | 7.05 | 6.46 | 10.8 | 11.6 | 11.1 |  | 5 | 0.1 | 0 | 4
5 | 5878777 | 2.09 | 3.6 | 0.6 | 0.00 | 2000 | 3000 | CLEAR | 29.1 | 0 |  |  | F | F | F | 7.42 | 7.16 | 6.4 | 11.3 | 11.9 | 10.6 |  | 17 | 0.1 | 0 | 5 | [14 empty] | 52342 | 3 | 3.5 | 27.9 | 33 | 24 | 1575 | 12.43 | 24 | EGYPT | STORE | [13 empty] | Week 3 | 20 | 426.174 | 31.3333 | 658.91 |  | 0.0057143
6 | 5880844 | 2.067 | 3.6 | 0.6 | 0.00 | 1000 | 2000 | CLEAR | 4.8 | 0 | [5 empty] | 7.44 | 7.27 | 6.89 | 10.3 | 9.5 | 7.7 |  | 10 | 0.1 | 0.01 | 6 | [26 empty] | pH | Reporting : | - | - | - | 6.04 | - | 6.89 | (s.u.) | 0 | 01/01 | GR
7 | 5882902 | 2.058 | 3.8 | 0.6 | 0.00 | 0 | 4000 | CLEAR | 7.2 | 0 |  |  | F | F | F | 7.32 | 7.24 | 6.54 | 10.8 | 10.1 | 8.3 |  | 7.5 | 0.1 | 0.01 | 7 | 329 | 5646.8639 |  |  | 13 | 223.1284 | 11 | 266 | 4565.5495 |  |  | 12 | 205.9646 | [13 empty] | Effluent | Permit : | - | - | - | 6 | - | 8.5 | (s.u.) | - | 01/01 | GR | Week 4 | 12.6667 | 290.3349 | 12 | 274.8197 |  | 0.0014286
8 | 5884974 | 2.072 | 3.6 | 0.6 | 0.00 | 0 | 1000 | CLEAR | 5.6 | 0 | [5 empty] | 7.33 | 7.22 | 6.36 | 11.9 | 10 | 8.2 |  | 7 | 0.01 | 0.01 | 8 | 277 | 4786.693 |  |  | 17 | 293.7682 | 14 | 252 | 4354.681 |  |  | 20 | 345.6096 |  | 47078 | 3 | 3.25 | 24.8 | 31 | 24 | 1657.5 | 12.34 | 24 | EGYPT | STORE
9 | 5887022 | 2.048 | 3.8 | 0.6 | 0.00 | 1000 | 1500 | CLEAR | 16.8 | 0 | [5 empty] | 7.42 | 7.25 | 6.46 | 10.2 | 10.4 | 8.4 |  | 10 | 0.01 | 0 | 9 | 285 | 4867.8912 | 185 | 3159.8592 | 14 | 239.1245 | 12 | 288 | 4919.1322 | 89 | 1520.1485 | 19 | 324.5261 | [25 empty] | Week 5 | 13 | 371.2662 | 15 | 427.5028 |  | 0
10 | 5889021 | 1.999 | 3.8 | 0.8 | 0.00 | 0 | 1000 | CLEAR | 34.7 | 0.03 | [5 empty] | 7.19 | 7.23 | 6.38 | 10.5 | 10.4 | 10.4 |  | 7 | 0 | 0 | 10
11 | 5891112 | 2.091 | 4.2 | 0.6 | 0.00 | 0 | 0 | LT RAIN | 41.3 | 0.29 |  |  | F | F | F | 6.94 | 7.13 | 6.4 | 9.7 | 9.6 | 10.5 |  | 3 | 0.01 | 0.01 | 11 | [26 empty] | TSS | Reporting : | 421.3851 | 824.2172 | (lbs / day) | 19.8571 | 31.3333 | 37 | (mg / L) | 0 | 03/07 | 24
12 | 5893366 | 2.254 | 3.6 | 0.6 | 0.00 | 1200 | 4000 | CLEAR | 36.8 | 0 | [5 empty] | 7.28 | 7.06 | 6.33 | 10.7 | 10.8 | 10.5 |  | 5 | 0.01 | 0 | 12 | [14 empty] | 50109 | 2 | 3.5 | 24.8 | 35 | 24 | 1680 | 12.4 | 24 | EGYPT | STORE |  | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24 | Maximum | 20 | 426.174 | 31.3333 | 658.91 |  | 0.0057143
13 | 5895568 | 2.202 | 3.8 | 0.6 | 0.00 | 1000 | 0 | CLEAR | 39.1 | 0 |  |  | O | O | O | 7.12 | 7.11 | 6.56 | 10.7 | 10.2 | 10.5 |  | 6 | 0.01 | 0 | 13
14 | 5897751 | 2.183 | 4 | 0.8 | 0.00 | 1000 | 3000 | LT RAIN | 46.4 | 0.07 | [5 empty] | 7.12 | 7.05 | 6.19 | 9.8 | 10.1 | 10.6 |  | 4.5 | 0.01 | 0.01 | 14 | 236 | 4296.6679 |  |  | 20 | 364.1244 | 16 | 204 | 3714.0689 |  |  | 37 | 673.6301
15 | 5900422 | 2.671 | 4.6 | 1 | 0.00 | 1000 | 8500 | RAIN | 41.9 | 0.26 |  |  | R | R | R | 6.88 | 6.92 | 6.24 | 10.2 | 10.7 | 11.2 |  | 6 | 0.01 | 0.01 | 15 | 208 | 4633.4371 |  |  | 26 | 579.1796 | 19 | 260 | 5791.7964 |  |  | 37 | 824.2172 |  | 31881 | 3 | 2.25 | 15.5 | 26 | 11 |  |  | 11 | Hawk Ridge | COMPOST
16 | 5903293 | 2.871 | 4.2 | 1 | 0.00 | 0 | 0 | CLEAR | 23.8 | 0 | [5 empty] | 6.84 | 6.92 | 6.54 | 10.1 | 10 | 9.2 |  | 6 | 0.1 | 0 | 16 | 194 | 4645.1632 | 121 | 2897.2409 | 14 | 335.218 | 13 | 218 | 5219.8225 | 68 | 1628.2015 | 20 | 478.8828 | [13 empty] | SETTLEABLE
17 | 5905957 | 2.664 | 4.6 | 1 | 0.00 | 0 | 0 | SLEET | 28.4 | 0.34 | [5 empty] | 6.85 | 6.95 | 6.59 | 9.5 | 6.1 | 6 |  | 5 | 0.01 | 0.01 | 17 | [26 empty] | SOLIDS | Reporting : | - | - | - | - | 0.0057143 | 0.01 | (mg / L) | 0 | 01/01 | GR
18 | 5908685 | 2.728 | 4.6 | 0.8 | 0.00 | 0 | 0 | LT SNOW | 27.1 | 0.13 | [5 empty] | 6.76 | 6.82 | 6.67 | 9.5 | 9.3 | 8 |  | 4 | 0.01 | 0 | 18 | [26 empty] | Effluent | Permit : | - | - | - | - | (Report) | 0.3 | (mg / L) | - | 01/01 | GR
19 | 5911339 | 2.654 | 4.1 | 0.8 | 0.00 | 1600 | 5500 | CLOUDY | 31 | 0.27 |  |  | S | S | S | 6.89 | 6.8 | 6.86 | 10.6 | 10.4 | 9.1 |  | 3 | 0.01 | 0.01 | 19 | [14 empty] | 58274 | 4 | 3.75 | 27.9 | 27 | 20 |  |  | 20 | Hawk Ridge | COMPOST
20 | 5913928 | 2.589 | 4.2 | 0.8 | 0.00 | 3500 | 3000 | CLEAR | 32.7 | 0.39 | [5 empty] | 6.88 | 7.1 | 6.76 | 10.3 | 11.5 | 10.4 |  | 7.5 | 0.01 | 0 | 20
21 | 5916585 | 2.657 | 4.4 | 0.8 | 0.00 | 0 | 1000 | CLEAR | 25.9 | 0.04 |  |  | E | E | E | 6.93 | 6.94 | 6.69 | 9.7 | 9.5 | 9 |  | 6.5 | 0.1 | 0 | 21 | 243 | 5384.7293 |  |  | 12 | 265.9126 | 10 | 240 | 5318.2512 |  |  | 12 | 265.9126
22 | 5919172 | 2.587 | 5.2 | 1.2 | 0.00 | 2000 | 1500 | CLOUDY | 41.7 | 0.01 | [5 empty] | 6.94 | 7.01 | 6.55 | 10.2 | 10.1 | 9.3 |  | 7.5 | 0.01 | 0 | 22 | 181 | 3905.18 |  |  | 13 | 280.4825 | 11 | 164 | 3538.3951 |  |  | 12 | 258.907 |  | 34396 | 3 | 4.25 | 15.5 | 27 | 11 |  |  | 11 | Hawk Ridge | COMPOST |  | FLOW | Reporting : | 2.6067 | 3.53 | (MGD) | - | - | - | - | 0 | 99/99 | RC |  |  |  | CBOD
23 | 5922166 | 2.994 | 4.8 | 1.4 | 0.00 | 3200 | 2500 | CLEAR | 46.9 | 0 |  |  | A | A | A | 6.57 | 6.71 | 6.26 | 10.3 | 10 | 11.3 |  | 4.5 | 0.01 | 0 | 23 | 193 | 4819.2023 | 113 | 2821.6055 | 13 | 324.6095 | 13 | 374 | 9338.765 | 76 | 1897.717 | 12 | 299.6395 | [13 empty] | Effluent | Permit : | 3.85 | (Report) | (MGD) | - | - | - | - | - | 99/99 | RC
24 | 5925450 | 3.284 | 4.8 | 1.4 | 0.00 | 2500 | 0 | CLEAR | 36.7 | 0.03 | [5 empty] | 6.46 | 6.54 | 6.55 | 9.8 | 10 | 10.5 |  | 2.5 | 0.01 | 0 | 24 | [41 empty] | % Removal
25 | 5928692 | 3.242 | 5 | 1.5 | 0.00 | 0 | 0 | CLEAR | 37.3 | 0.09 |  |  | S | S | S | 6.58 | 6.65 | 6.71 | 9.8 | 10.3 | 10.5 |  | 3 | 0.01 | 0 | 25
26 | 5931991 | 3.299 | 4.8 | 1.6 | 0.00 | 200 | 4750 | CLEAR | 37.2 | 0.18 | [5 empty] | 6.79 | 6.75 | 6.69 | 10.1 | 10.2 | 10.3 |  | 4.5 | 0.01 | 0 | 26 | [14 empty] | 53071 | 4 | 3.5 | 24.8 | 28 | 20 |  |  | 20 | Hawk Ridge | COMPOST | [16 empty] | 94.5488
27 | 5935451 | 3.46 | 5 | 1.4 | 0.00 | 1200 | 2000 | CLOUDY | 43.4 | 0.01 |  |  | O | O | O | 6.69 | 6.79 | 6.77 | 9.7 | 9.3 | 10.5 |  | 4 | 0.01 | 0 | 27 | [26 empty] | BOD, 5-day | Reporting : | - | - | - | 93.5147 | - | - | (percent) | 0 | 01/30 | CA
28 | 5938928 | 3.477 | 6.4 | 1.5 | 0.00 | 5200 | 2000 | CLEAR | 42.4 | 0 | [5 empty] | 6.62 | 6.66 | 6.78 | 10 | 11.5 | 11.6 |  | 4 | 0.01 | 0 | 28 | 194 | 5625.6469 |  |  | 13 | 376.9763 | 11 | 242 | 7017.5596 |  |  | 16 | 463.9709 | [13 empty] | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
29 | 5942458 | 3.53 | 5 | 1.4 | 0.00 | 4000 | 4500 | CLEAR | 38 | 0 |  |  | N | N | N | 6.74 | 6.79 | 6.75 | 10.2 | 9.4 | 9.3 |  | 7 | 0.01 | 0 | 29 | 194 | 5711.3988 |  |  | 13 | 382.7226 | 10 | 218 | 6417.9636 |  |  | 13 | 382.7226 |  | 30215 | 3 | 2 | 15.5 | 28 | 10 |  |  | 10 | Hawk Ridge | COMPOST
30 | 5945724 | 3.266 | 5.4 | 1.2 | 0.00 | 3700 | 1000 | CLEAR | 41.5 | 0 | [5 empty] | 6.67 | 6.69 | 6.72 | 9.7 | 10.6 | 10.2 |  | 6.5 | 0.01 | 0 | 30 | 224 | 6101.4106 | 113 | 3077.9437 | 13 | 354.0997 | 11 | 254 | 6918.5638 | 51 | 1389.1604 | 16 | 435.815
31 | 5948925 | 3.201 | 5 | 1.2 | 0.00 | 0 | 0 | CLEAR | 40.1 | 0 | [5 empty] | 6.51 | 6.38 | 6.56 | 11.4 | 9.7 | 9.5 |  | 5 | 0.01 | 0 | 31
[53 empty] | TSS | Reporting : | - | - | - | 92.0023 | - | - | (percent) | 0 | 01/30 | CA
Total | 80808 | 80.808 | - | - | 0 | 35300 | 66750 | - | - | 3.07 | 0.0 |  | 0 | - | - | - | - | - | - | - | - |  | - | - | - | Total | - | - | - | - | - | - | - | - | - | - | - | - | - |  | 397799 | - | 28.75 | 198.4 | - | 168 | 6150 | - | 168 | - | - |  | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
Maximum | - | 3.53 | 6.4 | 1.6 | 0 | 5200 | 8500 | - | 46.9 | 0.48 | - |  | - | - | - | 7.44 | 7.27 | 6.89 | 11.9 | 11.9 | 11.6 |  | 17 | 0.1 | 0.01 | Maximum | 329 | 6101.4106 | 193 | 3441.3676 | 26 | 579.1796 | 19 | 374 | 9338.765 | 93 | 1897.717 | 37 | 824.2172 |  | - | 4 | - | - | 35 | - | - | 12.43 | - | - | -
Minimum | - | 1.999 | 3.6 | 0.6 | 0 | 0 | 0 | - | 4.8 | 0 | - |  | - | - | - | 6.46 | 6.38 | 6.04 | 9.5 | 6.1 | 6 |  | 2.5 | 0 | 0 | Minimum | 181 | 3905.18 | 113 | 2821.6055 | 12 | 223.1284 | 10 | 164 | 3538.3951 | 51 | 1389.1604 | 12 | 205.9646 |  | - | 2 | - | - | 26 | - | - | 12.34 | - | - | -
Average | - | 2.6067 | 4.3774 | 0.92903 | 0.000 | 1138.7097 | 2153.2258 | - | 32.3968 | 0.099032 | - |  | - | - | - | 6.9574 | 6.96 | 6.5345 | 10.3935 | 10.1774 | 9.8129 |  | 6.1129 | 0.027097 | 0.0025806 | Average | 240.5714 | 5102.7027 | 145 | 3079.6034 | 15.3571 | 330.9241 | 12.7857 | 248.2857 | 5432.763 | 75.4 | 1618.7006 | 19.8571 | 421.3851 |  | 44199.8889 | 3.2222 | 3.1944 | 22.0444 | 29.7778 | 18.6667 | 1537.5 | 12.3875 | 18.6667 | - | -
[13 empty] | Geometric Mean : |  | - | [14 empty] | Percent Removal : |  | 93.5147 |  |  |  | Percent Removal : |  | 92.0023

## Graph Mar07
Plant Capacity
3.85 mgd

## April 07
BRUNSWICK SEWER DISTRICT | [11 empty] | State Discharge License Number W 002600-5L-C-R | [9 empty] | Certifying Official: |  |  | Francis E. McVey | BRUNSWICK SEWER DISTRICT | [13 empty] | State Discharge License Number W 002600-5L-C-R | [11 empty] | BRUNSWICK SEWER DISTRICT | [9 empty] | State Discharge License Number W 002600-5L-C-R
Monthly Report of Treatment Operations : |  |  |  |  | April | 2007 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [12 empty] | General Manager | Monthly Report of Treatment Operations : |  |  |  |  | April | 2007 | [7 empty] | N.P.D.E.S. Permit Number ME 0100102 | [9 empty] | Page 2. |  | Monthly Report of Treatment Operations : |  |  | April | 2007 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [7 empty] | Page 3.
SETTLEABLE
| FLOW | [6 empty] | WEATHER |  |  |  |  | DISINFECTION |  |  | P.H. |  |  | TEMPERATURE |  |  |  | SOLIDS |  |  |  | BIOCHEMICAL OXYGEN DEMAND | [6 empty] | TOTAL SUSPENDED SOLIDS | [6 empty] | SLUDGE DEWATERING | [7 empty] | SLUDGE UTILIZATION |  |  |  | SUMMARY DATA | [11 empty] | HIGH WEEKLY AVERAGE VALUES
|  | Total | Maxim. | Minim. | [8 empty] | Hypo - | [37 empty] | Stored |  |  |  | LOADING |  |  | CONCENTRATION |  |  |  | REPORTING |  |  |  | BOD |  | TSS |  |  | SETTLEABLE SOLIDS
| Totalizer | Flow | Flow | Flow | Flow | Holding | Septic |  | Average | Total | Grit |  | chlorite | Chlorine | [18 empty] | CBOD | [7 empty] | Quantity | Feed | Filter |  | Cake | Sludge | Lime | Average | Quantity |  | or |  |  |  | Monthly | Daily |  | Mo Aver | High Wkly | Daily |  |  |  | Sample
Date | Reading | Treated | (instant.) | (instant.) | By-passed | Received | Added | Conditions | Temp. | Precip. | Removed |  | Used | Residual | E. Coli | Influent | Primary | Effluent | Influent | Primary | Effluent |  | Influent | Primary | Effluent | Date | Influent | Influent | Primary | Primary | Effluent | Effluent | Effluent | Influent | Influent | Primary | Primary | Effluent | Effluent |  | Dewatered | Solids | Operation | Polymer | Dry Solid | Dewatered | Added | pH | Utilized | Site | Spread |  |  |  | Average | Maximum | Units | Minimum | Average | Maximum | Units | Exceptions | Frequency | Type |  | High Weekly Average |  | High Weekly Average |  |  | High Weekly Average
|  | (MG) | (MG) | (MG) | (MG) | (gallons) | (gallons) |  | (deg. F.) | (inches) | (cu. yd.) |  | (gallons) | (mg/L) | (#/100) | (s.u.) | (s.u.) | (s.u.) | (deg. C.) | (deg. C.) | (deg. C.) |  | (ml/L) | (ml/L) | (ml/L) |  | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) |  | (gallons) | (%) | (hours) | (lbs) | (%) | (cu. yd.) | (lbs) | (s.u.) | (cu. yd.) | [16 empty] | (mg / L) | (lbs / day) | (mg / L) | (lbs / day) |  | (mg / L)
5948925
1 | 5952007 | 3.082 | 4.8 | 1.2 | 0.00 | 0 | 0 | CLEAR | 39 | 0 | [5 empty] | 6.43 | 6.73 | 6.75 | 9.9 | 9.1 | 10.2 |  | 2 | 0.01 | 0 | 1 | [26 empty] | BOD, 5-day | Reporting : | 440.024 | 1009.3902 | (lbs / day) | 11.5833 | 12 | 14 | (mg / L) | 0 | 03/07 | 24 | Week 1 | 11 | 276.521 | 13.6667 | 343.6024 |  | 0.0042857 | check formulas for designation of weeks
2 | 5955093 | 3.086 | 4.6 | 1.2 | 0.00 | 700 | 1500 | LT RAIN | 37 | 0.14 | [5 empty] | 6.62 | 6.81 | 6.85 | 10.6 | 11 | 10.9 |  | 4 | 0.01 | 0 | 2 | [14 empty] | 57595 | 2 | 3.75 | 27.9 | 28 | 20 |  |  | 20 | HawkRidge | COMPOST |  | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24
3 | 5958127 | 3.034 | 4.7 | 1.1 | 0.00 | 2700 | 4000 | LT RAIN | 35 | 0.09 |  |  | O | O | O | 6.79 | 6.79 | 6.75 | 10.1 | 9.7 | 10.6 |  | 7 | 0.01 | 0.01 | 3 | [38 empty] | Week 2 | 12 | 316.1138 | 11.6667 | 307.2706 |  | 0.0042857 | identifies cell for keyed data entry
4 | 5961145 | 3.018 | 4.6 | 1.1 | 0.00 | 1700 | 4000 | CLOUDY | 33 | 0.15 | [5 empty] | 6.56 | 6.69 | 6.7 | 10.6 | 10 | 10.7 |  | 2.5 | 0.01 | 0.01 | 4 | 210 | 5285.7252 |  |  | 12 | 302.0414 | 10 | 268 | 6745.5922 |  |  | 13 | 327.2116 |  | 27298 | 3 | 2 | 15.5 | 28 | 10 |  |  | 10 | HawkRidge | COMPOST
5 | 5964179 | 3.034 | 4.4 | 1.1 | 0.00 | 0 | 0 | SNOW | 33 | 0.5 |  |  | F | F | F | 6.94 | 6.94 | 6.89 | 10.2 | 9.5 | 8.3 |  | 7.5 | 0.01 | 0 | 5 | 184 | 4655.855 |  |  | 10 | 253.0356 | 9 | 156 | 3947.3554 |  |  | 14 | 354.2498 | [25 empty] | Week 3 | 11.6667 | 733.4307 | 17 | 1090.1409 |  | 0.0014286
6 | 5967171 | 2.992 | 4.6 | 1.4 | 0.00 | 200 | 0 | CLEAR | 33 | 0.26 | [5 empty] | 6.7 | 6.82 | 6.74 | 10.2 | 9.5 | 9.9 |  | 3.5 | 0 | 0 | 6 | 189 | 4716.1699 | 103 | 2570.1878 | 11 | 274.4861 | 9 | 154 | 3842.8051 | 53 | 1322.5238 | 14 | 349.3459 | [13 empty] | pH | Reporting : | - | - | - | 6.16 | - | 6.91 | (s.u.) | 0 | 01/01 | GR
7 | 5970391 | 3.22 | 4.8 | 1.3 | 0.00 | 0 | 0 | CLEAR | 34 | 0 |  |  | F | F | F | 6.65 | 6.71 | 6.74 | 9.8 | 9.1 | 10 |  | 2.5 | 0.01 | 0.01 | 7 | [26 empty] | Effluent | Permit : | - | - | - | 6 | - | 8.5 | (s.u.) | - | 01/01 | GR | Week 4 | 11.6667 | 434.0303 | 12.3333 | 459.901 |  | 0
8 | 5973649 | 3.258 | 4.8 | 1.3 | 0.00 | 0 | 0 | CLEAR | 33 | 0 | [5 empty] | 6.76 | 6.85 | 6.91 | 10.5 | 9.1 | 10.7 |  | 3 | 0 | 0 | 8
9 | 5976826 | 3.177 | 4.6 | 1.2 | 0.00 | 0 | 4000 | CLOUDY | 38 | 0 | [5 empty] | 6.82 | 6.68 | 6.87 | 10.6 | 10 | 10.1 |  | 9 | 0 | 0.01 | 9 | [14 empty] | 61650 | 3 | 3.75 | 27.9 | 28 | 20 |  |  | 20 | HawkRidge | COMPOST | [13 empty] | Week 5
10 | 5980028 | 3.202 | 4.6 | 1.2 | 0.00 | 1850 | 5000 | CLEAR | 38 | 0 | [5 empty] | 6.92 | 6.92 | 6.83 | 10.4 | 9 | 9.7 |  | 11 | 0.3 | 0 | 10
11 | 5983183 | 3.155 | 5.3 | 1.2 | 0.00 | 2700 | 6500 | CLEAR | 37 | 0 |  |  | F | F | F | 6.85 | 6.89 | 6.8 | 10.2 | 9.9 | 10.5 |  | 5 | 0 | 0 | 11 | 199 | 5236.2273 |  |  | 11 | 289.4397 | 9 | 172 | 4525.7844 |  |  | 11 | 289.4397 | [13 empty] | TSS | Reporting : | 550.2287 | 1658.2839 | (lbs / day) | 13.6667 | 17 | 23 | (mg / L) | 1 | 03/07 | 24
12 | 5986364 | 3.181 | 4.7 | 1.2 | 0.00 | 1000 | 3000 | RAIN | 33 | 0.04 | [5 empty] | 6.43 | 6.64 | 6.6 | 10.4 | 9.5 | 9.8 |  | 6.5 | 0.01 | 0 | 12 | 211 | 5597.7329 |  |  | 12 | 318.3545 | 9 | 166 | 4403.9036 |  |  | 11 | 291.8249 | [13 empty] | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24 | Maximum | 12 | 733.4307 | 17 | 1090.1409 |  | 0.0042857
13 | 5989505 | 3.141 | 4.6 | 1.6 | 0.00 | 0 | 1500 | CLOUDY | 38 | 0.79 |  |  | O | O | O | 6.76 | 6.79 | 6.68 | 10.1 | 9.6 | 10.1 |  | 5 | 0.01 | 0.01 | 13 | 199 | 5212.9921 | 102 | 2671.9859 | 13 | 340.5472 | 11 | 180 | 4715.2692 | 38 | 995.4457 | 13 | 340.5472 |  | 38028 | 2 | 2.25 | 15.5 | 28 | 10 |  |  | 10 | HawkRidge | COMPOST
14 | 5992935 | 3.43 | 5 | 1.6 | 0.00 | 0 | 0 | CLEAR | 44 | 0 | [5 empty] | 6.48 | 6.62 | 6.67 | 9.9 | 9.8 | 10.3 |  | 2 | 0.01 | 0.01 | 14
15 | 5996395 | 3.46 | 8.6 | 1.9 | 0.00 | 0 | 0 | CLOUDY | 36 | 0.7 |  |  | R | R | R | 6.32 | 6.59 | 6.64 | 9.6 | 10 | 10.6 |  | 2 | 0.01 | 0 | 15
16 | 6000649 | 4.254 | 12 | 7.2 | 0.00 | 0 | 1000 | RAIN | 41 | 4.91 | [5 empty] | 6.22 | 6.35 | 6.62 | 8.7 | 8.5 | 9.5 |  | 3 | 0.3 | 0.01 | 16 | [26 empty] | SETTLEABLE
17 | 6010419 | 9.77 | 10.1 | 6.4 | 0.00 | 0 | 10500 | LT RAIN | 37.7 | 0.9 | [5 empty] | 6.67 | 6.64 | 6.63 | 9.3 | 9.1 | 9.3 |  | 0.9 | 0.4 | 0 | 17 | [14 empty] | 62007 | 3 | 3.75 | 31 | 28 | 20 |  |  | 20 | HawkRidge | COMPOST |  | SOLIDS | Reporting : | - | - | - | - | 0.0042857 | 0.01 | (mg / L) | 0 | 01/01 | GR
18 | 6019064 | 8.645 | 9.4 | 5.2 | 0.00 | 7500 | 5000 | CLOUDY | 42.7 | 0.1 | [5 empty] | 6.49 | 6.45 | 6.51 | 9.8 | 10.3 | 10 |  | 1.5 | 0.01 | 0 | 18 | 212 | 15285.0516 |  |  | 14 | 1009.3902 | 12 | 88 | 6344.7384 |  |  | 23 | 1658.2839 | [13 empty] | Effluent | Permit : | - | - | - | - | (Report) | 0.3 | (mg / L) | - | 01/01 | GR
19 | 6026418 | 7.354 | 8 | 4.1 | 0.00 | 4400 | 5200 | CLEAR | 47.6 | 0.02 |  |  | S | S | S | 6.51 | 6.49 | 6.59 | 10 | 9.9 | 10.6 |  | 2 | 0.01 | 0 | 19 | 76 | 4661.2594 |  |  | 9 | 551.9912 | 8 | 79 | 4845.2564 |  |  | 15 | 919.9854 |  | 31641 | 4 | 2.5 | 15.5 | 31 | 10 |  |  | 10 | HawkRidge | COMPOST
20 | 6032802 | 6.384 | 7.4 | 3.6 | 0.00 | 6750 | 4500 | CLEAR | 48.5 | 0 | [5 empty] | 6.69 | 6.63 | 6.65 | 9.7 | 9.4 | 9.9 |  | 2 | 0.01 | 0 | 20 | 88 | 4685.3453 | 84 | 4472.375 | 12 | 638.9107 | 10 | 116 | 6176.137 | 52 | 2768.6131 | 13 | 692.1533
21 | 6038638 | 5.836 | 7.2 | 3.2 | 0.00 | 0 | 2000 | CLEAR | 55.9 | 0 |  |  | E | E | E | 6.64 | 6.59 | 6.62 | 9.9 | 9.6 | 10.1 |  | 4 | 0.01 | 0 | 21
22 | 6043956 | 5.318 | 6.6 | 2.9 | 0.00 | 0 | 0 | CLEAR | 49.1 | 0 | [5 empty] | 6.21 | 6.32 | 6.51 | 9.3 | 9.3 | 10.4 |  | 1.5 | 0.01 | 0 | 22 | [26 empty] | FLOW | Reporting : | 4.3748 | 9.77 | (MGD) | - | - | - | - | 1 | 99/99 | RC |  |  |  | CBOD
23 | 6049020 | 5.064 | 6.4 | 2.8 | 0.00 | 0 | 4000 | CLEAR | 57.8 | 0 |  |  | A | A | A | 6.46 | 6.52 | 6.51 | 10.1 | 9.5 | 10.6 |  | 4 | 0.01 | 0 | 23 | [14 empty] | 48454 | 3 | 3 | 21.7 | 29 | 10 |  |  | 10 | HawkRidge | COMPOST |  | Effluent | Permit : | 3.85 | (Report) | (MGD) | - | - | - | - | - | 99/99 | RC
24 | 6053948 | 4.928 | 6.8 | 2.6 | 0.00 | 0 | 10700 | CLEAR | 58.8 | 0 | [5 empty] | 6.68 | 6.65 | 6.56 | 10.3 | 10.3 | 11.8 |  | 4.5 | 0.01 | 0 | 24 | [41 empty] | % Removal
25 | 6058601 | 4.653 | 6.2 | 2.4 | 0.00 | 4250 | 8750 | CLEAR | 48.1 | 0 |  |  | S | S | S | 6.46 | 6.41 | 6.4 | 10.9 | 11.3 | 11.1 |  | 7.5 | 0.2 | 0 | 25 | 147 | 5704.4849 |  |  | 10 | 388.0602 | 8 | 362 | 14047.7792 |  |  | 12 | 465.6722
26 | 6063067 | 4.466 | 6.4 | 2.6 | 0.00 | 5000 | 6500 | CLEAR | 46.7 | 0 | [5 empty] | 6.45 | 6.61 | 6.59 | 10.3 | 10.3 | 10.7 |  | 2.5 | 0.2 | 0 | 26 | 153 | 5698.7053 |  |  | 12 | 446.9573 | 10 | 194 | 7225.8094 |  |  | 12 | 446.9573 |  | 29095 | 4 | 2 | 15.5 | 26 | 10 |  |  | 10 | HawkRidge | COMPOST | [16 empty] | 94.2004
27 | 6067375 | 4.308 | 6.2 | 2.2 | 0.00 | 1300 | 6000 | RAIN | 43.9 | 0.31 |  |  | O | O | O | 6.47 | 6.42 | 6.41 | 10.9 | 10.1 | 11 |  | 3.5 | 0.01 | 0 | 27 | 140 | 5030.0208 | 113 | 4059.9454 | 13 | 467.0734 | 9 | 172 | 6179.7398 | 59 | 2119.7945 | 13 | 467.0734 | [13 empty] | BOD, 5-day | Reporting : | - | - | - | 92.6427 | - | - | (percent) | 0 | 01/30 | CA
28 | 6071570 | 4.195 | 6.2 | 2.6 | 0.00 | 0 | 3000 | CLOUDY | 47.1 | 0.12 | [5 empty] | 6.39 | 6.44 | 6.49 | 11.1 | 11.2 | 12.1 |  | 2.5 | 0.01 | 0 | 28 | [26 empty] | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
29 | 6075790 | 4.22 | 6.2 | 2.4 | 0.00 | 0 | 0 | LT RAIN | 44.5 | 0.77 |  |  | N | N | N | 6.05 | 6.14 | 6.16 | 10.1 | 10.2 | 11.2 |  | 1.5 | 0.1 | 0 | 29
30 | 6080169 | 4.379 | 6.2 | 2.4 | 0.00 | 7000 | 6500 | LT RAIN | 45 | 0.19 | [5 empty] | 6.46 | 6.4 | 6.37 | 11 | 11.1 | 11.8 |  | 3 | 0.01 | 0 | 30 | [14 empty] | 46139 | 4 | 3.25 | 24.8 | 34 | 24 | 1560 | 12.36 | 24 | EGYPT | STORE
31 | [25 empty] | 31
[53 empty] | TSS | Reporting : | - | - | - | 92.2164 | - | - | (percent) | 0 | 01/30 | CA
Total | 131244 | 131.244 | - | - | 0 | 47050 | 103150 | - | - | 9.99 | 0.0 |  | 0 | - | - | - | - | - | - | - | - |  | - | - | - | Total | - | - | - | - | - | - | - | - | - | - | - | - | - |  | 401907 | - | 26.25 | 195.3 | - | 134 | 1560 | - | 134 | - | - |  | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
Maximum | - | 9.77 | 12 | 7.2 | 0 | 7500 | 10700 | - | 58.8 | 4.91 | - |  | - | - | - | 6.94 | 6.94 | 6.91 | 11.1 | 11.3 | 12.1 |  | 11 | 0.4 | 0.01 | Maximum | 212 | 15285.0516 | 113 | 4472.375 | 14 | 1009.3902 | 12 | 362 | 14047.7792 | 59 | 2768.6131 | 23 | 1658.2839 |  | - | 4 | - | - | 34 | - | - | 12.36 | - | - | -
Minimum | - | 2.992 | 4.4 | 1.1 | 0 | 0 | 0 | - | 33 | 0 | - |  | - | - | - | 6.05 | 6.14 | 6.16 | 8.7 | 8.5 | 8.3 |  | 0.9 | 0 | 0 | Minimum | 76 | 4655.855 | 84 | 2570.1878 | 9 | 253.0356 | 8 | 79 | 3842.8051 | 38 | 995.4457 | 11 | 289.4397 |  | - | 2 | - | - | 26 | - | - | 12.36 | - | - | -
Average | - | 4.3748 | 6.2 | 2.4067 | 0.000 | 1568.3333 | 3438.3333 | - | 41.8467 | 0.333 | - |  | - | - | - | 6.5627 | 6.6177 | 6.6347 | 10.15 | 9.83 | 10.4167 |  | 3.88 | 0.056667 | 0.0023333 | Average | 167.3333 | 5980.7975 | 100.5 | 3443.6235 | 11.5833 | 440.024 | 9.5 | 175.5833 | 6083.3475 | 50.5 | 1801.5943 | 13.6667 | 550.2287 |  | 44656.3333 | 3.1111 | 2.9167 | 21.7 | 28.8889 | 14.8889 | 1560 | 12.36 | 14.8889 | - | -
[13 empty] | Geometric Mean : |  | - | [14 empty] | Percent Removal : |  | 92.6427 |  |  |  | Percent Removal : |  | 92.2164

## Graph Apr07
Plant Capacity
3.85 mgd

## May 07
BRUNSWICK SEWER DISTRICT | [11 empty] | State Discharge License Number W 002600-5L-C-R | [9 empty] | Certifying Official: |  |  | Francis E. McVey | BRUNSWICK SEWER DISTRICT | [13 empty] | State Discharge License Number W 002600-5L-C-R | [11 empty] | BRUNSWICK SEWER DISTRICT | [9 empty] | State Discharge License Number W 002600-5L-C-R
Monthly Report of Treatment Operations : |  |  |  |  | May | 2007 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [12 empty] | General Manager | Monthly Report of Treatment Operations : |  |  |  |  | May | 2007 | [7 empty] | N.P.D.E.S. Permit Number ME 0100102 | [9 empty] | Page 2. |  | Monthly Report of Treatment Operations : |  |  | May | 2007 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [7 empty] | Page 3.
SETTLEABLE
| FLOW | [6 empty] | WEATHER |  |  |  |  | DISINFECTION |  |  | P.H. |  |  | TEMPERATURE |  |  |  | SOLIDS |  |  |  | BIOCHEMICAL OXYGEN DEMAND | [6 empty] | TOTAL SUSPENDED SOLIDS | [6 empty] | SLUDGE DEWATERING | [7 empty] | SLUDGE UTILIZATION |  |  |  | SUMMARY DATA | [11 empty] | HIGH WEEKLY AVERAGE VALUES
|  | Total | Maxim. | Minim. | [8 empty] | Hypo - | [37 empty] | Stored |  |  |  | LOADING |  |  | CONCENTRATION |  |  |  | REPORTING |  |  |  | BOD |  | TSS |  |  | SETTLEABLE SOLIDS
| Totalizer | Flow | Flow | Flow | Flow | Holding | Septic |  | Average | Total | Grit |  | chlorite | Chlorine | [18 empty] | CBOD | [7 empty] | Quantity | Feed | Filter |  | Cake | Sludge | Lime | Average | Quantity |  | or |  |  |  | Monthly | Daily |  | Mo Aver | High Wkly | Daily |  |  |  | Sample
Date | Reading | Treated | (instant.) | (instant.) | By-passed | Received | Added | Conditions | Temp. | Precip. | Removed |  | Used | Residual | E. Coli | Influent | Primary | Effluent | Influent | Primary | Effluent |  | Influent | Primary | Effluent | Date | Influent | Influent | Primary | Primary | Effluent | Effluent | Effluent | Influent | Influent | Primary | Primary | Effluent | Effluent |  | Dewatered | Solids | Operation | Polymer | Dry Solid | Dewatered | Added | pH | Utilized | Site | Spread |  |  |  | Average | Maximum | Units | Minimum | Average | Maximum | Units | Exceptions | Frequency | Type |  | High Weekly Average |  | High Weekly Average |  |  | High Weekly Average
|  | (MG) | (MG) | (MG) | (MG) | (gallons) | (gallons) |  | (deg. F.) | (inches) | (cu. yd.) |  | (gallons) | (mg/L) | (#/100) | (s.u.) | (s.u.) | (s.u.) | (deg. C.) | (deg. C.) | (deg. C.) |  | (ml/L) | (ml/L) | (ml/L) |  | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) |  | (gallons) | (%) | (hours) | (lbs) | (%) | (cu. yd.) | (lbs) | (s.u.) | (cu. yd.) | [16 empty] | (mg / L) | (lbs / day) | (mg / L) | (lbs / day) |  | (mg / L)
6080169
1 | 6084552 | 4.383 | 5.8 | 2.2 | 0.00 | 2950 | 8500 | CLEAR | 50 | 0 |  |  | OFF FOR SEASON | OFF FOR SEASON | OFF FOR SEASON | 6.62 | 6.69 | 6.68 | 11.2 | 10.6 | 11.4 |  | 6.5 | 0.1 | 0 | 1 | [26 empty] | BOD, 5-day | Reporting : | 336.8752 | 490.9841 | (lbs / day) | 11.5714 | 14 | 17 | (mg / L) | 0 | 03/07 | 24 | Week 1 | 11.3333 | 383.5399 | 13 | 437.8722 |  | 0 | check formulas for designation of weeks
2 | 6088752 | 4.2 | 5.8 | 2 | 0.00 | 500 | 7000 | CLOUDY | 52.5 | 0 | [5 empty] | 6.64 | 6.7 | 6.56 | 11.5 | 11.3 | 12.1 |  | 8.5 | 0.01 | 0 | 2 | 150 | 5254.2 |  |  | 11 | 385.308 | 9 | 136 | 4763.808 |  |  | 10 | 350.28 | [13 empty] | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24
3 | 6092824 | 4.072 | 6 | 2 | 0.00 | 200 | 9000 | CLEAR | 51 | 0 | [5 empty] | 6.61 | 6.49 | 6.53 | 10.8 | 10.9 | 11.4 |  | 5 | 0.01 | 0 | 3 | 157 | 5331.7954 |  |  | 12 | 407.5258 | 10 | 200 | 6792.096 |  |  | 14 | 475.4467 |  | 34776 | 4 | 3.25 | 18.6 | 33 | 23 | 1560 | 12.35 | 23 | EGYPT | STORE | [13 empty] | Week 2 | 14 | 411.4011 | 21 | 618.0107 |  | 0.0057143 | identifies cell for keyed data entry
4 | 6096724 | 3.9 | 5.4 | 1.8 | 0.00 | 2500 | 8750 | CLEAR | 52.9 | 0 | [5 empty] | 6.51 | 6.58 | 6.56 | 11 | 10.6 | 11.4 |  | 3.5 | 0.01 | 0 | 4 | 208 | 6765.408 | 114 | 3707.964 | 11 | 357.786 | 9 | 246 | 8001.396 | 69 | 2244.294 | 15 | 487.89
5 | 6100475 | 3.751 | 5.4 | 1.8 | 0.00 | 0 | 0 | CLEAR | 53.7 | 0 | [5 empty] | 6.3 | 6.61 | 6.57 | 10.6 | 10.6 | 11.8 |  | 2.5 | 0.01 | 0 | 5 | [38 empty] | Week 3 | 10.6667 | 296.5871 | 21.6667 | 602.1619 |  | 0.0028571
6 | 6104129 | 3.654 | 5.2 | 1.6 | 0.00 | 0 | 0 | CLEAR | 45.9 | 0.11 | [5 empty] | 6.44 | 6.54 | 6.53 | 10.7 | 10.5 | 11.6 |  | 3 | 0.01 | 0.01 | 6 | [26 empty] | pH | Reporting : | - | - | - | 6.21 | - | 6.68 | (s.u.) | 0 | 01/01 | GR
7 | 6107732 | 3.603 | 5.4 | 1.6 | 0.00 | 2500 | 5750 | CLEAR | 50.2 | 0.01 | [5 empty] | 6.58 | 6.62 | 6.6 | 11.4 | 11.2 | 12 |  | 3.5 | 0.01 | 0 | 7 | [14 empty] | 47849 | 2 | 3.25 | 24.8 | 33 | 24 | 1560 | 12.4 | 24 | EGYPT | STORE |  | Effluent | Permit : | - | - | - | 6 | - | 8.5 | (s.u.) | - | 01/01 | GR | Week 4 | 10.6667 | 294.2408 | 22.3333 | 617.4519 |  | 0.0028571
8 | 6111299 | 3.567 | 5.6 | 1.6 | 0.00 | 3300 | 11750 | CLEAR | 56.2 | 0 | [5 empty] | 6.53 | 6.53 | 6.49 | 11.8 | 11.3 | 12.4 |  | 4.5 | 0.01 | 0 | 8
9 | 6114938 | 3.639 | 5 | 1.6 | 0.00 | 8000 | 10250 | CLEAR | 62.4 | 0 | [5 empty] | 6.45 | 6.49 | 6.4 | 12.2 | 11.7 | 12.9 |  | 4.5 | 0.01 | 0.01 | 9 | 216 | 6555.4402 |  |  | 13 | 394.5404 | 11 | 332 | 10075.9543 |  |  | 21 | 637.3345 | [25 empty] | Week 5
10 | 6118401 | 3.463 | 5.4 | 1.6 | 0.00 | 4200 | 10500 | CLEAR | 64 | 0 | [5 empty] | 6.82 | 6.76 | 6.53 | 12.3 | 12.2 | 13.7 |  | 6 | 0.1 | 0.01 | 10 | 213 | 6151.7425 |  |  | 17 | 490.9841 | 14 | 228 | 6584.9638 |  |  | 21 | 606.5098 |  | 20617 | 4 | 2 | 9.3 | 34 | 12 | 900 | 12.33 | 12 | EGYPT | STORE
11 | 6121885 | 3.484 | 6.2 | 1.6 | 0.00 | 9550 | 9900 | RAIN | 57.2 | 0.38 | [5 empty] | 6.47 | 6.49 | 6.46 | 12.2 | 12.4 | 13.9 |  | 5.5 | 0.1 | 0.01 | 11 | 206 | 5985.6514 | 112 | 3254.3347 | 12 | 348.6787 | 10 | 252 | 7322.2531 | 88 | 2556.9773 | 21 | 610.1878 | [13 empty] | TSS | Reporting : | 571.2983 | 699.309 | (lbs / day) | 20 | 22.3333 | 26 | (mg / L) | 0 | 03/07 | 24
12 | 6125264 | 3.379 | 4.4 | 1.6 | 0.00 | 0 | 0 | CLEAR | 54.3 | 0 | [5 empty] | 6.42 | 6.41 | 6.34 | 11.7 | 11.8 | 12.7 |  | 2 | 0.01 | 0 | 12 | [26 empty] | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24 | Maximum | 14 | 411.4011 | 22.3333 | 618.0107 |  | 0.0057143
13 | 6128457 | 3.193 | 5 | 1.6 | 0.00 | 4000 | 3000 | CLEAR | 53.7 | 0 | [5 empty] | 6.51 | 6.49 | 6.39 | 11.9 | 11.8 | 12.3 |  | 7 | 0.01 | 0 | 13
14 | 6131618 | 3.161 | 5 | 1.6 | 0.00 | 2600 | 6500 | CLEAR | 52.7 | 0 | [5 empty] | 6.59 | 6.53 | 6.5 | 12.6 | 12.8 | 13.6 |  | 16 | 0.1 | 0 | 14 | [14 empty] | 27126 | 3 | 1.75 | 15.5 | 32 | 12 | 735 | 12.38 | 12 | EGYPT | STORE
15 | 6134852 | 3.234 | 4.8 | 1.5 | 0.00 | 3100 | 11000 | CLOUDY | 53.3 | 0.13 |  |  | 34.5 | 0.54 | 2 | 6.58 | 6.5 | 6.31 | 12.5 | 11.9 | 13 |  | 5 | 0.1 | 0.01 | 15
16 | 6138085 | 3.233 | 4.6 | 1.5 | 0.00 | 2500 | 6500 | RAIN | 50.2 | 1.06 |  |  | 36 | 0.48 | 2 | 6.62 | 6.66 | 6.42 | 12.4 | 12.3 | 13.6 |  | 5 | 0.01 | 0 | 16 | 243 | 6552.0625 |  |  | 10 | 269.6322 | 10 | 310 | 8358.5982 |  |  | 21 | 566.2276 | [13 empty] | SETTLEABLE
17 | 6141551 | 3.466 | 4.8 | 1.4 | 0.00 | 3000 | 9000 | CLOUDY | 43.4 | 0.05 |  |  | 34.6 | 0.67 | 13.4 | 6.52 | 6.37 | 6.44 | 12.4 | 12.5 | 13.1 |  | 4 | 0.6 | 0.01 | 17 | 238 | 6879.7327 |  |  | 10 | 289.0644 | 9 | 242 | 6995.3585 |  |  | 20 | 578.1288 |  | 41865 | 3 | 3.25 | 21.7 | 34 | 24 | 1560 | 12.34 | 24 | EGYPT | STORE |  | SOLIDS | Reporting : | - | - | - | - | 0.0057143 | 0.01 | (mg / L) | 0 | 01/01 | GR
18 | 6144859 | 3.308 | 4.8 | 1.8 | 0.00 | 3700 | 8000 | RAIN | 41.8 | 0.88 |  |  | 35.5 | 0.5 |  | 6.51 | 6.49 | 6.45 | 12.4 | 12.1 | 12.6 |  | 4 | 0.01 | 0 | 18 | 206 | 5683.2763 | 118 | 3255.469 | 12 | 331.0646 | 11 | 264 | 7283.4221 | 84 | 2317.4525 | 24 | 662.1293 | [13 empty] | Effluent | Permit : | - | - | - | - | (Report) | 0.3 | (mg / L) | - | 01/01 | GR
19 | 6148503 | 3.644 | 5 | 1.8 | 0.00 | 0 | 0 | RAIN | 51.6 | 0.13 |  |  | 35.1 | 0.49 |  | 6.3 | 6.42 | 6.34 | 11.9 | 11.7 | 12.6 |  | 4.5 | 0.01 | 0 | 19
20 | 6152141 | 3.638 | 4.8 | 1.6 | 0.00 | 0 | 0 | RAIN | 50.5 | 0.1 |  |  | 40 | 0.43 |  | 6.27 | 6.38 | 6.31 | 11.9 | 12 | 12.9 |  | 2 | 0.01 | 0 | 20
21 | 6155704 | 3.563 | 4.8 | 1.6 | 0.00 | 2100 | 6000 | CLEAR | 51.8 | 0.06 |  |  | 38.2 | 0.6 | 3.1 | 6.54 | 6.52 | 6.45 | 12.5 | 11.7 | 12.8 |  | 6.5 | 0.1 | 0.01 | 21 | [14 empty] | 55558 | 3 | 4.25 | 31 | 33 | 36 | 2040 | 12.38 | 36 | EGYPT | STORE
22 | 6159155 | 3.451 | 5 | 1.4 | 0.00 | 4100 | 7750 | CLEAR | 52.7 | 0 |  |  | 32.6 | 0.48 | 35 | 6.6 | 6.57 | 6.52 | 13 | 12.5 | 13 |  | 5.5 | 0.01 | 0 | 22 | [26 empty] | FLOW | Reporting : | 3.4535 | 4.383 | (MGD) | - | - | - | - | 0 | 99/99 | RC |  |  |  | CBOD
23 | 6162514 | 3.359 | 6.1 | 1.3 | 0.00 | 5300 | 6000 | CLOUDY | 50.1 | 0 |  |  | 38.1 | 0.46 | 4.1 | 6.46 | 6.51 | 6.48 | 12.7 | 12.7 | 13.8 |  | 4 | 0.1 | 0 | 23 | 177 | 4958.4886 |  |  | 10 | 280.1406 | 9 | 248 | 6947.4869 |  |  | 23 | 644.3234 | [13 empty] | Effluent | Permit : | 3.85 | (Report) | (MGD) | - | - | - | - | - | 99/99 | RC
24 | 6165892 | 3.378 | 5.8 | 1.4 | 0.00 | 2400 | 12500 | CLEAR | 56.5 | 0 |  |  | 33.9 | 0.42 |  | 6.58 | 6.71 | 6.62 | 12.9 | 12.9 | 13.5 |  | 12 | 0.1 | 0 | 24 | 194 | 5465.4689 |  |  | 10 | 281.7252 | 8 | 324 | 9127.8965 |  |  | 22 | 619.7954 |  | 44189 | 3 | 4.5 | 24.8 | 34 | 36 | 2565 | 12.41 | 36 | EGYPT | STORE | [16 empty] | % Removal
25 | 6169098 | 3.206 | 5.2 | 1.3 | 0.00 | 1000 | 8000 | CLEAR | 74.6 | 0 |  |  | 34.7 | 0.39 |  | 6.48 | 6.5 | 6.39 | 13.2 | 12.9 | 14.5 |  | 6.5 | 0.1 | 0.01 | 25 | 186 | 4973.2754 | 111 | 2967.9224 | 12 | 320.8565 | 12 | 228 | 6096.2731 | 79 | 2112.3052 | 22 | 588.2369
26 | 6172387 | 3.289 | 4.8 | 1.2 | 0.00 | 2000 | 2000 | CLOUDY | 73 | 0 |  |  | 35.7 | 0.5 |  | 6.26 | 6.32 | 6.33 | 15 | 14.9 | 16.1 |  | 2.5 | 0.01 | 0 | 26 | [41 empty] | 94.99
27 | 6175378 | 2.991 | 4.6 | 1.3 | 0.00 | 0 | 0 | CLEAR | 59.5 | 0 |  |  | 32.7 | 0.38 |  | 6.07 | 6.18 | 6.21 | 13.5 | 13.8 | 15 |  | 2 | 0.01 | 0 | 27 | [26 empty] | BOD, 5-day | Reporting : | - | - | - | 94.1859 | - | - | (percent) | 0 | 01/30 | CA
28 | 6178268 | 2.89 | 4.4 | 1.2 | 0.00 | 0 | 0 | CLOUDY | 64 | 0.09 |  |  | 28.9 | 0.74 |  | 6.11 | 6.18 | 6.22 | 13.2 | 13.4 | 14.5 |  | 1.5 | 0.1 | 0 | 28 | [26 empty] | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
29 | 6181170 | 2.902 | 5.8 | 1 | 0.00 | 3000 | 5500 | CLEAR | 65.4 | 0 |  |  | 25.9 | 0.58 | 1 | 6.66 | 6.73 | 6.46 | 13.7 | 13.4 | 14.7 |  | 5 | 0.1 | 0 | 29 | [14 empty] | 52180 | 3 | 3.5 | 27.9 | 35 | 24 | 1785 | 12.37 | 24 | EGYPT | STORE
30 | 6184395 | 3.225 | 4.4 | 1 | 0.00 | 3200 | 8250 | CLEAR | 63.7 | 0.01 |  |  | 29.9 | 0.42 | 3 | 6.57 | 6.57 | 6.25 | 13.7 | 13.5 | 14.7 |  | 6 | 0.1 | 0 | 30 | 210 | 5648.265 |  |  | 12 | 322.758 | 10 | 260 | 6993.09 |  |  | 26 | 699.309
31 | 6187227 | 2.832 | 4.4 | 1 | 0.00 | 6400 | 13500 | LT RAIN | 60 | 0 |  |  | 26.5 | 0.53 | 4.1 | 6.58 | 6.62 | 6.38 | 13.5 | 13.7 | 15.4 |  | 5 | 0.2 | 0 | 31 | 208 | 4912.727 |  |  | 10 | 236.1888 | 9 | 248 | 5857.4822 |  |  | 20 | 472.3776 |  | 41840 | 3 | 3 | 21.7 | 33 | 24 | 1530 | 12.42 | 24 | EGYPT | STORE
[53 empty] | TSS | Reporting : | - | - | - | 92.0409 | - | - | (percent) | 0 | 01/30 | CA
Total | 107058 | 107.058 | - | - | 0 | 82100 | 194900 | - | - | 3.01 | 0.0 |  | 572.8 | - | - | - | - | - | - | - | - |  | - | - | - | Total | - | - | - | - | - | - | - | - | - | - | - | - | - |  | 366000 | - | 28.75 | 195.3 | - | 215 | 14235 | - | 215 | - | - |  | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
Maximum | - | 4.383 | 6.2 | 2.2 | 0 | 9550 | 13500 | - | 74.6 | 1.06 | - |  | - | 0.74 | 35 | 6.82 | 6.76 | 6.68 | 15 | 14.9 | 16.1 |  | 16 | 0.6 | 0.01 | Maximum | 243 | 6879.7327 | 118 | 3707.964 | 17 | 490.9841 | 14 | 332 | 10075.9543 | 88 | 2556.9773 | 26 | 699.309 |  | - | 4 | - | - | 35 | - | - | 12.42 | - | - | -
Minimum | - | 2.832 | 4.4 | 1 | 0 | 0 | 0 | - | 41.8 | 0 | - |  | - | 0.38 | 1 | 6.07 | 6.18 | 6.21 | 10.6 | 10.5 | 11.4 |  | 1.5 | 0.01 | 0 | Minimum | 150 | 4912.727 | 111 | 2967.9224 | 10 | 236.1888 | 8 | 136 | 4763.808 | 69 | 2112.3052 | 10 | 350.28 |  | - | 2 | - | - | 32 | - | - | 12.33 | - | - | -
Average | - | 3.4535 | 5.1516 | 1.5323 | 0.000 | 2648.3871 | 6287.0968 | - | 55.4452 | 0.097097 | - |  | - | - | - | 6.4903 | 6.5213 | 6.4426 | 12.3323 | 12.1806 | 13.1935 |  | 5.129 | 0.07 | 0.0025806 | Average | 200.8571 | 5794.1096 | 113.75 | 3296.4225 | 11.5714 | 336.8752 | 10.0714 | 251.2857 | 7228.577 | 80 | 2307.7572 | 20 | 571.2983 |  | 40666.6667 | 3.1111 | 3.1944 | 21.7 | 33.4444 | 23.8889 | 1581.6667 | 12.3756 | 23.8889 | - | -
[53 empty] | CHLORINE | Reporting : | - | - | - | - | - | 0.74 | - | 0 | 02/01 | GR
[13 empty] | Geometric Mean : |  | 4.0502 | [14 empty] | Percent Removal : |  | 94.1859 |  |  |  | Percent Removal : |  | 92.0409 | [14 empty] | Effluent | Permit : | - | - | - | - | - | 0.86 | (mg/L) | - | 02/01 | GR

## Graph May07
Plant Capacity
3.85 mgd

## June 07
BRUNSWICK SEWER DISTRICT | [11 empty] | State Discharge License Number W 002600-5L-C-R | [9 empty] | Certifying Official: |  |  | Francis E. McVey | BRUNSWICK SEWER DISTRICT | [13 empty] | State Discharge License Number W 002600-5L-C-R | [11 empty] | BRUNSWICK SEWER DISTRICT | [9 empty] | State Discharge License Number W 002600-5L-C-R
Monthly Report of Treatment Operations : |  |  |  |  | June | 2007 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [12 empty] | General Manager | Monthly Report of Treatment Operations : |  |  |  |  | June | 2007 | [7 empty] | N.P.D.E.S. Permit Number ME 0100102 | [9 empty] | Page 2. |  | Monthly Report of Treatment Operations : |  |  | June | 2007 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [7 empty] | Page 3.
SETTLEABLE
| FLOW | [6 empty] | WEATHER |  |  |  |  | DISINFECTION |  |  | P.H. |  |  | TEMPERATURE |  |  |  | SOLIDS |  |  |  | BIOCHEMICAL OXYGEN DEMAND | [6 empty] | TOTAL SUSPENDED SOLIDS | [6 empty] | SLUDGE DEWATERING | [7 empty] | SLUDGE UTILIZATION |  |  |  | SUMMARY DATA | [11 empty] | HIGH WEEKLY AVERAGE VALUES
|  | Total | Maxim. | Minim. | [8 empty] | Hypo - | [37 empty] | Stored |  |  |  | LOADING |  |  | CONCENTRATION |  |  |  | REPORTING |  |  |  | BOD |  | TSS |  |  | SETTLEABLE SOLIDS
| Totalizer | Flow | Flow | Flow | Flow | Holding | Septic |  | Average | Total | Grit |  | chlorite | Chlorine | [18 empty] | CBOD | [7 empty] | Quantity | Feed | Filter |  | Cake | Sludge | Lime | Average | Quantity |  | or |  |  |  | Monthly | Daily |  | Mo Aver | High Wkly | Daily |  |  |  | Sample
Date | Reading | Treated | (instant.) | (instant.) | By-passed | Received | Added | Conditions | Temp. | Precip. | Removed |  | Used | Residual | E. Coli | Influent | Primary | Effluent | Influent | Primary | Effluent |  | Influent | Primary | Effluent | Date | Influent | Influent | Primary | Primary | Effluent | Effluent | Effluent | Influent | Influent | Primary | Primary | Effluent | Effluent |  | Dewatered | Solids | Operation | Polymer | Dry Solid | Dewatered | Added | pH | Utilized | Site | Spread |  |  |  | Average | Maximum | Units | Minimum | Average | Maximum | Units | Exceptions | Frequency | Type |  | High Weekly Average |  | High Weekly Average |  |  | High Weekly Average
|  | (MG) | (MG) | (MG) | (MG) | (gallons) | (gallons) |  | (deg. F.) | (inches) | (cu. yd.) |  | (gallons) | (mg/L) | (#/100) | (s.u.) | (s.u.) | (s.u.) | (deg. C.) | (deg. C.) | (deg. C.) |  | (ml/L) | (ml/L) | (ml/L) |  | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) |  | (gallons) | (%) | (hours) | (lbs) | (%) | (cu. yd.) | (lbs) | (s.u.) | (cu. yd.) | [16 empty] | (mg / L) | (lbs / day) | (mg / L) | (lbs / day) |  | (mg / L)
6187227
1 | 6190068 | 2.841 | 4.8 | 1 | 0.00 | 10200 | 6000 | CLOUDY | 66.8 | 0.01 |  |  | 26.3 | 0.45 |  | 6.57 | 6.6 | 6.07 | 13.8 | 13.6 | 14.4 |  | 6 | 0.1 | 0.01 | 1 | 212 | 5023.1153 | 147 | 3483.0092 | 12 | 284.3273 | 10 | 276 | 6539.5274 | 90 | 2132.4546 | 26 | 616.0424 | [13 empty] | BOD, 5-day | Reporting : | 327.8428 | 437.85 | (lbs / day) | 13.1538 | 15.3333 | 18 | (mg / L) | 0 | 03/07 | 24 | Week 1 | 11 | 281 | 24 | 596 |  | 0 | check formulas for designation of weeks
2 | 6192892 | 2.824 | 9.3 | 1.8 | 0.00 | 0 | 3000 | LT RAIN | 65.4 | 1.41 |  |  | 23.9 | 0.34 |  | 6.45 | 6.51 | 6.39 | 13 | 13.5 | 15.1 |  | 3.5 | 0.1 | 0.01 | 2 | [26 empty] | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24
3 | 6196055 | 3.163 | 4.6 | 1.1 | 0.00 | 0 | 0 | CLOUDY | 53.6 | 0.13 |  |  | 25.1 | 0.38 |  | 6.36 | 6.45 | 6.36 | 13.3 | 13.4 | 14.7 |  | 5 | 0.01 | 0.01 | 3 | [38 empty] | Week 2 | 13.6667 | 406.8308 | 30 | 890.3367 |  | 0.0028571 | identifies cell for keyed data entry
4 | 6199059 | 3.004 | 5.4 | 2 | 0.00 | 4400 | 7000 | RAIN | 52.4 | 1.14 |  |  | 27.7 | 0.48 | 5.2 | 6.48 | 6.43 | 6.34 | 13.6 | 13.4 | 13.8 |  | 5 | 0.01 | 0.01 | 4 | [14 empty] | 44108 | 3 | 3 | 21.7 | 34 | 24 | 1620 | 12.35 | 24 | EGYPT | STORE
5 | 6202818 | 3.759 | 5.6 | 1.6 | 0.00 | 4400 | 11500 | CLEAR | 58.9 | 0.18 |  |  | 35.1 | 0.39 | 9.6 | 6.48 | 6.43 | 6.33 | 14.1 | 14.3 | 15 |  | 4.5 | 0.1 | 0 | 5 | [38 empty] | Week 3 | 15.3333 | 371.4386 | 30.6667 | 743.2525 |  | 0.0014286
6 | 6206568 | 3.75 | 5.6 | 1.5 | 0.00 | 4000 | 16250 | CLEAR | 58.6 | 0 |  |  | 36.8 | 0.49 | 3 | 6.57 | 6.53 | 6.3 | 13.8 | 13.5 | 14.6 |  | 7 | 0.2 | 0 | 6 | 190 | 5942.25 |  |  | 14 | 437.85 | 12 | 274 | 8569.35 |  |  | 28 | 875.7 | [13 empty] | pH | Reporting : | - | - | - | 6.07 | - | 7.02 | (s.u.) | 0 | 01/01 | GR
7 | 6210180 | 3.612 | 4.8 | 1.4 | 0.00 | 1400 | 6000 | CLEAR | 56.4 | 0 |  |  | 40 | 0.42 |  | 6.9 | 6.89 | 6.42 | 13.9 | 14.1 | 15.1 |  | 6 | 0.2 | 0 | 7 | 203 | 6115.1882 |  |  | 13 | 391.613 | 10 | 278 | 8374.4942 |  |  | 29 | 873.5983 |  | 60392 | 3 | 4.5 | 27.9 | 33 | 36 | 2430 | 12.38 | 36 | EGYPT | STORE |  | Effluent | Permit : | - | - | - | 6 | - | 8.5 | (s.u.) | - | 01/01 | GR | Week 4 | 12.6667 | 304.4739 | 30.6667 | 738.0344 |  | 0.0028571
8 | 6213529 | 3.349 | 5.4 | 1.2 | 0.00 | 2000 | 5000 | CLEAR | 60.5 | 0 |  |  | 33.7 | 0.46 |  | 6.72 | 6.79 | 6.36 | 14 | 14.3 | 15.4 |  | 5.5 | 0.1 | 0 | 8 | 277 | 7736.7928 | 136 | 3798.5698 | 14 | 391.0292 | 12 | 274 | 7653.0008 | 90 | 2513.7594 | 33 | 921.7118
9 | 6216793 | 3.264 | 4.6 | 1.3 | 0.00 | 0 | 3000 | CLOUDY | 56.9 | 0 |  |  | 35.4 | 0.34 |  | 6.42 | 6.53 | 6.2 | 13.4 | 13.8 | 15.6 |  | 2.5 | 0.01 | 0 | 9 | [38 empty] | Week 5 | 11.3333 | 243.1332 | 23 | 494.0366 |  | 0.0014286
10 | 6219798 | 3.005 | 4.6 | 1.4 | 0.00 | 0 | 0 | CLEAR | 65.1 | 0 |  |  | 30.1 | 0.44 |  | 6.51 | 6.5 | 6.39 | 13.4 | 13.5 | 14.7 |  | 3 | 0.01 | 0 | 10
11 | 6222883 | 3.085 | 5.4 | 1.4 | 0.00 | 4500 | 5750 | CLEAR | 69.2 | 0.13 |  |  | 29.8 | 0.48 | 3.1 | 6.51 | 6.49 | 6.43 | 15.8 | 15.7 | 16.2 |  | 5.5 | 0.1 | 0 | 11 | [14 empty] | 60242 | 5 | 4 | 31 | 33 | 36 | 2280 | 12.4 | 36 | EGYPT | STORE |  | TSS | Reporting : | 708.6941 | 943.9045 | (lbs / day) | 28.3846 | 30.6667 | 39 | (mg / L) | 0 | 03/07 | 24
12 | 6226211 | 3.328 | 4.4 | 1 | 0.00 | 2500 | 9000 | CLEAR | 67.2 | 0.01 |  |  | 35.3 | 0.46 | 161.6 | 6.83 | 6.45 | 6.18 | 14.6 | 15.3 | 16.9 |  | 8.5 | 0.01 | 0 | 12 | [26 empty] | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24 | Maximum | 15.3333 | 406.8308 | 30.6667 | 890.3367 |  | 0.0028571
13 | 6229168 | 2.957 | 4.5 | 1 | 0.00 | 1400 | 11000 | CLOUDY | 58.5 | 0.01 |  |  | 38.3 | 0.55 | 1 | 6.93 | 6.77 | 6.23 | 15 | 14.4 | 15.8 |  | 6.5 | 0.1 | 0 | 13 | 216 | 5326.8581 |  |  | 11 | 271.2752 | 11 | 430 | 10604.3934 |  |  | 22 | 542.5504
14 | 6232043 | 2.875 | 5.8 | 1.6 | 0.00 | 2000 | 13000 | CLOUDY | 57.2 | 0 |  |  | 28.9 | 0.55 |  | 7.1 | 6.93 | 6.29 | 14.6 | 14.5 | 15.9 |  | 8 | 0.7 | 0 | 14 | 258 | 6186.195 |  |  | 18 | 431.595 | 15 | 376 | 9015.54 |  |  | 31 | 743.3025 |  | 60575 | 3 | 4.25 | 27.9 | 31 | 36 | 2422.5 | 12.41 | 36 | EGYPT | STORE
15 | 6234945 | 2.902 | 4.6 | 1 | 0.00 | 4900 | 9000 | CLEAR | 59.3 | 0 |  |  | 26 | 0.4 |  | 7.17 | 6.91 | 6.33 | 14.8 | 14 | 15.2 |  | 9 | 0.1 | 0.01 | 15 | 242 | 5857.0486 | 146 | 3533.5913 | 17 | 411.4456 | 15 | 388 | 9390.6398 | 121 | 2928.5243 | 39 | 943.9045
16 | 6237730 | 2.785 | 4.4 | 1 | 0.00 | 2000 | 2000 | CLEAR | 62.2 | 0 |  |  | 24.1 | 0.45 |  | 6.85 | 6.85 | 6.24 | 13.5 | 13.9 | 14.9 |  | 5 | 0.01 | 0 | 16 | [26 empty] | SETTLEABLE
17 | 6240394 | 2.664 | 4.3 | 1 | 0.00 | 0 | 0 | CLEAR | 67.6 | 0.17 |  |  | 22.4 | 0.46 |  | 6.83 | 6.83 | 6.32 | 13.5 | 13.7 | 15.6 |  | 1 | 0.01 | 0 | 17 | [26 empty] | SOLIDS | Reporting : | - | - | - | - | 0.0028571 | 0.01 | (mg / L) | 0 | 01/01 | GR
18 | 6243122 | 2.728 | 5.4 | 1.6 | 0.00 | 5000 | 9250 | CLEAR | 69.1 | 0 |  |  | 23.6 | 0.61 | 1 | 6.88 | 6.81 | 6.27 | 14.5 | 15.1 | 16 |  | 4 | 0.1 | 0 | 18 | [26 empty] | Effluent | Permit : | - | - | - | - | (Report) | 0.3 | (mg / L) | - | 01/01 | GR
19 | 6245857 | 2.735 | 4.8 | 1 | 0.00 | 2000 | 7000 | CLEAR | 64.9 | 0 |  |  | 24.4 | 0.46 | 1 | 6.79 | 6.78 | 6.3 | 15.3 | 15.6 | 16.6 |  | 4 | 0.2 | 0 | 19 | [14 empty] | 76151 | 4 | 5.75 | 43.4 | 34 | 48 | 3277.5 | 12.36 | 48 | EGYPT | STORE
20 | 6248695 | 2.838 | 5.6 | 1.6 | 0.00 | 0 | 13500 | CLEAR | 63.9 | 0.01 |  |  | 30.3 | 0.47 | 25.6 | 6.94 | 6.71 | 6.17 | 14.8 | 15.7 | 17.7 |  | 5 | 0.01 | 0.01 | 20 | 200 | 4733.784 |  |  | 13 | 307.696 | 12 | 354 | 8378.7977 |  |  | 28 | 662.7298
21 | 6251568 | 2.873 | 4.3 | 1 | 0.00 | 1550 | 8500 | CLEAR | 68.6 | 0 |  |  | 33.7 | 0.43 |  | 7 | 6.8 | 6.3 | 14.7 | 15.6 | 16.4 |  | 5.5 | 0.2 | 0.01 | 21 | 238 | 5702.6752 |  |  | 13 | 311.4907 | 10 | 376 | 9009.2683 |  |  | 32 | 766.7462 |  | 55024 | 4 | 3.25 | 27.9 | 28 | 30 | 1852.5 | 12.42 | 30 | EGYPT | STORE
22 | 6254508 | 2.94 | 5.2 | 1 | 0.00 | 2000 | 9000 | CLOUDY | 63.3 | 0.08 |  |  | 32 | 0.48 |  | 6.67 | 6.75 | 6.08 | 15.1 | 14.9 | 17.4 |  | 3 | 0.01 | 0 | 22 | 197 | 4830.3612 | 127 | 3113.9892 | 12 | 294.2352 | 11 | 320 | 7846.272 | 106 | 2599.0776 | 32 | 784.6272 | [13 empty] | FLOW | Reporting : | 2.9389 | 3.759 | (MGD) | - | - | - | - | 0 | 99/99 | RC |  |  |  | CBOD
23 | 6257446 | 2.938 | 4.4 | 1 | 0.00 | 0 | 0 | CLEAR | 60.5 | 0 |  |  | 28.9 | 0.52 |  | 6.86 | 6.89 | 6.55 | 15 | 14.7 | 16.1 |  | 2 | 0.01 | 0 | 23 | [26 empty] | Effluent | Permit : | 3.85 | (Report) | (MGD) | - | - | - | - | - | 99/99 | RC
24 | 6260043 | 2.597 | 4.3 | 1 | 0.00 | 0 | 0 | CLEAR | 65.1 | 0 |  |  | 23 | 0.5 |  | 6.64 | 6.76 | 6.58 | 14.6 | 14.6 | 15.7 |  | 1.5 | 0.01 | 0 | 24 | [41 empty] | % Removal
25 | 6262626 | 2.583 | 4.2 | 1 | 0.00 | 7000 | 9000 | LT RAIN | 65.1 | 0 |  |  | 22.1 | 0.39 | 9.6 | 7.02 | 6.88 | 6.41 | 15.4 | 15.1 | 16.4 |  | 5 | 0.01 | 0 | 25 | [14 empty] | 60530 | 3 | 4 | 24.8 | 31 | 36 | 3000 | 12.41 | 36 | EGYPT | STORE
26 | 6265234 | 2.608 | 4.7 | 1 | 0.00 | 0 | 9700 | CLEAR | 73.5 | 0 |  |  | 24.2 | 0.47 | 18.3 | 7.28 | 6.95 | 6.55 | 15.6 | 15.6 | 17.2 |  | 8 | 0.01 | 0.01 | 26 | [41 empty] | 95.2249
27 | 6267853 | 2.619 | 4.1 | 0.8 | 0.00 | 4800 | 11100 | CLEAR | 76.9 | 0 |  |  | 27.8 | 0.44 | 2 | 7.06 | 7.31 | 6.73 | 16.5 | 16.6 | 17.3 |  | 7.5 | 0.01 | 0 | 27 | 268 | 5853.7793 |  |  | 13 | 283.952 | 11 | 372 | 8125.3951 |  |  | 28 | 611.5889 | [13 empty] | BOD, 5-day | Reporting : | - | - | - | 94.3557 | - | - | (percent) | 0 | 01/30 | CA
28 | 6270364 | 2.511 | 4.6 | 0.8 | 0.00 | 3800 | 7500 | CLEAR | 77 | 0 |  |  | 35.8 | 0.4 |  | 6.87 | 7.49 | 6.75 | 15.4 | 16 | 18.1 |  | 6 | 0.01 | 0 | 28 | 293 | 6135.9298 |  |  | 11 | 230.3591 | 9 | 290 | 6073.1046 |  |  | 20 | 418.8348 |  | 43987 | 5 | 3 | 18.6 | 30 | 24 | 2160 | 12.36 | 24 | EGYPT | STORE |  | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
29 | 6272943 | 2.579 | 4.6 | 0.7 | 0.00 | 6100 | 6350 | CLEAR | 63.4 | 0 |  |  | 34 | 0.44 |  | 7.2 | 7.83 | 7.02 | 15.7 | 15.1 | 16.9 |  | 10 | 0.01 | 0 | 29 | 282 | 6065.4985 | 162 | 3484.4353 | 10 | 215.0886 | 9 | 390 | 8388.4554 | 110 | 2365.9746 | 21 | 451.6861
30 | 6275395 | 2.452 | 4 | 0.6 | 0.00 | 2350 | 2000 | CLEAR | 63.2 | 0 |  |  | 35.6 | 0.44 |  | 6.86 | 7.55 | 6.84 | 14.1 | 15.2 | 16.6 |  | 5 | 1 | 0 | 30
31 | [25 empty] | 31
[53 empty] | TSS | Reporting : | - | - | - | 91.6098 | - | - | (percent) | 0 | 01/30 | CA
Total | 88168 | 88.168 | - | - | 0 | 78300 | 200400 | - | - | 3.28 | 0.0 |  | 894.3 | - | - | - | - | - | - | - | - |  | - | - | - | Total | - | - | - | - | - | - | - | - | - | - | - | - | - |  | 461009 | - | 31.75 | 223.2 | - | 270 | 19042.5 | - | 270 | - | - |  | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
Maximum | - | 3.759 | 9.3 | 2 | 0 | 10200 | 16250 | - | 77 | 1.41 | - |  | - | 0.61 | 161.6 | 7.28 | 7.83 | 7.02 | 16.5 | 16.6 | 18.1 |  | 10 | 1 | 0.01 | Maximum | 293 | 7736.7928 | 162 | 3798.5698 | 18 | 437.85 | 15 | 430 | 10604.3934 | 121 | 2928.5243 | 39 | 943.9045 |  | - | 5 | - | - | 34 | - | - | 12.42 | - | - | -
Minimum | - | 2.452 | 4 | 0.6 | 0 | 0 | 0 | - | 52.4 | 0 | - |  | - | 0.34 | 1 | 6.36 | 6.43 | 6.07 | 13 | 13.4 | 13.8 |  | 1 | 0.01 | 0 | Minimum | 190 | 4733.784 | 127 | 3113.9892 | 10 | 215.0886 | 9 | 274 | 6073.1046 | 90 | 2132.4546 | 20 | 418.8348 |  | - | 3 | - | - | 28 | - | - | 12.35 | - | - | -
Average | - | 2.9389 | 4.9433 | 1.18 | 0.000 | 2610 | 6680 | - | 63.6767 | 0.10933 | - |  | - | - | - | 6.7917 | 6.8133 | 6.391 | 14.4933 | 14.6233 | 15.91 |  | 5.2667 | 0.11533 | 0.0026667 | Average | 236.6154 | 5808.4212 | 143.6 | 3482.7189 | 13.1538 | 327.8428 | 11.3077 | 338.3077 | 8305.2491 | 103.4 | 2507.9581 | 28.3846 | 708.6941 |  | 57626.125 | 3.75 | 3.9688 | 27.9 | 31.75 | 33.75 | 2380.3125 | 12.3863 | 33.75 | - | -
[53 empty] | CHLORINE | Reporting : | - | - | - | - | - | 0.61 | - | 0 | 02/01 | GR
[13 empty] | Geometric Mean : |  | 5.4421 | [14 empty] | Percent Removal : |  | 94.3557 |  |  |  | Percent Removal : |  | 91.6098 | [14 empty] | Effluent | Permit : | - | - | - | - | - | 0.86 | (mg/L) | - | 02/01 | GR

## Graph Jun07
Plant Capacity
3.85 mgd

## July 07
BRUNSWICK SEWER DISTRICT | [11 empty] | State Discharge License Number W 002600-5L-C-R | [9 empty] | Certifying Official: |  |  | Francis E. McVey | BRUNSWICK SEWER DISTRICT | [13 empty] | State Discharge License Number W 002600-5L-C-R | [11 empty] | BRUNSWICK SEWER DISTRICT | [9 empty] | State Discharge License Number W 002600-5L-C-R
Monthly Report of Treatment Operations : |  |  |  |  | July | 2007 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [12 empty] | General Manager | Monthly Report of Treatment Operations : |  |  |  |  | July | 2007 | [7 empty] | N.P.D.E.S. Permit Number ME 0100102 | [9 empty] | Page 2. |  | Monthly Report of Treatment Operations : |  |  | July | 2007 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [7 empty] | Page 3.
SETTLEABLE
| FLOW | [6 empty] | WEATHER |  |  |  |  | DISINFECTION |  |  | P.H. |  |  | TEMPERATURE |  |  |  | SOLIDS |  |  |  | BIOCHEMICAL OXYGEN DEMAND | [6 empty] | TOTAL SUSPENDED SOLIDS | [6 empty] | SLUDGE DEWATERING | [7 empty] | SLUDGE UTILIZATION |  |  |  | SUMMARY DATA | [11 empty] | HIGH WEEKLY AVERAGE VALUES
|  | Total | Maxim. | Minim. | [8 empty] | Hypo - | [37 empty] | Stored |  |  |  | LOADING |  |  | CONCENTRATION |  |  |  | REPORTING |  |  |  | BOD |  | TSS |  |  | SETTLEABLE SOLIDS
| Totalizer | Flow | Flow | Flow | Flow | Holding | Septic |  | Average | Total | Grit |  | chlorite | Chlorine | [18 empty] | CBOD | [7 empty] | Quantity | Feed | Filter |  | Cake | Sludge | Lime | Average | Quantity |  | or |  |  |  | Monthly | Daily |  | Mo Aver | High Wkly | Daily |  |  |  | Sample
Date | Reading | Treated | (instant.) | (instant.) | By-passed | Received | Added | Conditions | Temp. | Precip. | Removed |  | Used | Residual | E. Coli | Influent | Primary | Effluent | Influent | Primary | Effluent |  | Influent | Primary | Effluent | Date | Influent | Influent | Primary | Primary | Effluent | Effluent | Effluent | Influent | Influent | Primary | Primary | Effluent | Effluent |  | Dewatered | Solids | Operation | Polymer | Dry Solid | Dewatered | Added | pH | Utilized | Site | Spread |  |  |  | Average | Maximum | Units | Minimum | Average | Maximum | Units | Exceptions | Frequency | Type |  | High Weekly Average |  | High Weekly Average |  |  | High Weekly Average
|  | (MG) | (MG) | (MG) | (MG) | (gallons) | (gallons) |  | (deg. F.) | (inches) | (cu. yd.) |  | (gallons) | (mg/L) | (#/100) | (s.u.) | (s.u.) | (s.u.) | (deg. C.) | (deg. C.) | (deg. C.) |  | (ml/L) | (ml/L) | (ml/L) |  | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) |  | (gallons) | (%) | (hours) | (lbs) | (%) | (cu. yd.) | (lbs) | (s.u.) | (cu. yd.) | [16 empty] | (mg / L) | (lbs / day) | (mg / L) | (lbs / day) |  | (mg / L)
6275395
1 | 6277655 | 2.26 | 4 | 0.7 | 0.00 | 0 | 0 | CLOUDY | 61.6 | 0 |  |  | 35.4 | 0.45 | 2 | 6.84 | 8.24 | 6.79 | 14.1 | 15 | 16.4 |  | 3 | 0.1 | 0 | 1 | [26 empty] | BOD, 5-day | Reporting : | 192.8514 | 256.847 | (lbs / day) | 10.1667 | 11.3333 | 13 | (mg / L) | 0 | 03/07 | 24 | Week 1 | 8.6667 | 160.6896 | 17.3333 | 321.76 |  | 0.0028571 | check formulas for designation of weeks
2 | 6279930 | 2.275 | 4 | 0.8 | 0.00 | 2500 | 4700 | CLEAR | 62.5 | 0 |  |  | 38 | 0.6 | 1 | 7.05 | 7.58 | 6.85 | 15.3 | 16.3 | 17.2 |  | 8.5 | 0.01 | 0 | 2 | 276 | 5236.686 |  |  | 8 | 151.788 | 7 | 284 | 5388.474 |  |  | 16 | 303.576 |  | 80883 | 4 | 6 | 46.5 | 31 | 48 | 4500 | 12.36 | 36 | EGYPT | STORE |  | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24
3 | 6282236 | 2.306 | 4.8 | 0.6 | 0.00 | 10200 | 9100 | CLEAR | 62.3 | 0 |  |  | 32.6 | 0.45 | 6.3 | 7.16 | 6.98 | 7 | 15.8 | 15.3 | 17 |  | 11 | 0.01 | 0.01 | 3 | [22 empty] | 12 | EGYPT | STORE | [13 empty] | Week 2 | 9.6667 | 187.1246 | 19.3333 | 374.4966 |  | 0.0014286 | identifies cell for keyed data entry
4 | 6284601 | 2.365 | 4 | 0.8 | 0.00 | 2000 | 1000 | CLEAR | 62.6 | 0.04 |  |  | 30.2 | 0.43 |  | 6.68 | 7.77 | 6.81 | 16.3 | 16 | 17.1 |  | 2.5 | 0.01 | 0 | 4
5 | 6286725 | 2.124 | 3.8 | 0.6 | 0.00 | 2900 | 5000 | CLOUDY | 65.3 | 0.25 |  |  | 34.2 | 0.58 |  | 7.06 | 7.58 | 6.69 | 16 | 15.8 | 17.3 |  | 8 | 0.1 | 0.01 | 5 | 263 | 4658.8241 |  |  | 8 | 141.7133 | 7 | 324 | 5739.3878 |  |  | 15 | 265.7124 |  | 47475 | 4 | 3.5 | 18.6 | 34 | 24 | 2625 | 12.39 | 24 | EGYPT | STORE | [13 empty] | Week 3 | 11.3333 | 215.0775 | 19.6667 | 373.0649 |  | 0.0014286
6 | 6288986 | 2.261 | 7.2 | 0.7 | 0.00 | 7700 | 9500 | CLOUDY | 66.3 | 0.87 |  |  | 37 | 0.53 |  | 6.96 | 7.5 | 6.75 | 16.1 | 17.6 | 19.1 |  | 7.5 | 0.01 | 0 | 6 | 278 | 5242.1737 | 184 | 3469.6402 | 10 | 188.5674 | 9 | 340 | 6411.2916 | 101 | 1904.5307 | 21 | 395.9915 | [13 empty] | pH | Reporting : | - | - | - | 6.51 | - | 7.1 | (s.u.) | 0 | 01/01 | GR
7 | 6291444 | 2.458 | 4 | 0.6 | 0.00 | 0 | 0 | CLOUDY | 64.5 | 0.1 |  |  | 38.1 | 0.44 |  | 6.85 | 8.15 | 6.73 | 15.3 | 16 | 17.9 |  | 6 | 0.01 | 0 | 7 | [26 empty] | Effluent | Permit : | - | - | - | 6 | - | 8.5 | (s.u.) | - | 01/01 | GR | Week 4 | 11 | 208.5139 | 16 | 303.7845 |  | 0
8 | 6293679 | 2.235 | 3.8 | 0.6 | 0.00 | 0 | 0 | RAIN | 62.2 | 0.06 |  |  | 37 | 0.4 |  | 6.9 | 8.06 | 6.68 | 15.9 | 15.4 | 16.7 |  | 7.5 | 0.01 | 0 | 8
9 | 6295901 | 2.222 | 4.1 | 0.7 | 0.00 | 2200 | 8500 | CLOUDY | 59.8 | 0.62 |  |  | 35.6 | 0.51 | 15.8 | 7.13 | 8.27 | 6.77 | 16.3 | 16 | 17.4 |  | 8 | 0.01 | 0 | 9 | [14 empty] | 59207 | 3 | 3.5 | 24.8 | 33 | 24 | 1785 | 12.39 | 24 | EGYPT | STORE | [13 empty] | Week 5
10 | 6298284 | 2.383 | 4.2 | 0.6 | 0.00 | 2400 | 7950 | CLOUDY | 62.6 | 0 |  |  | 40.3 | 0.39 | 18.9 | 7.09 | 7.57 | 7.03 | 16.3 | 16.5 | 17.7 |  | 8 | 0.01 | 0 | 10
11 | 6300593 | 2.309 | 4.2 | 0.6 | 0.00 | 3400 | 10250 | CLOUDY | 65.5 | 0.01 |  |  | 39.2 | 0.4 | 16 | 6.67 | 7.5 | 6.74 | 16.3 | 16.1 | 17.7 |  | 3.5 | 0.01 | 0.01 | 11 | 278 | 5353.4627 |  |  | 9 | 173.3135 | 9 | 362 | 6971.0557 |  |  | 18 | 346.6271 | [13 empty] | TSS | Reporting : | 343.2765 | 434.6641 | (lbs / day) | 18.0833 | 19.6667 | 22 | (mg / L) | 0 | 03/07 | 24
12 | 6302964 | 2.371 | 4.4 | 0.7 | 0.00 | 3200 | 11000 | CLOUDY | 69.4 | 0.02 |  |  | 44.9 | 0.38 |  | 7 | 7.41 | 6.7 | 15.3 | 16.1 | 17.5 |  | 6 | 0.01 | 0 | 12 | 306 | 6050.8868 |  |  | 10 | 197.7414 | 8 | 408 | 8067.8491 |  |  | 21 | 415.2569 |  | 51329 | 3 | 3 | 37.2 | 31 | 24 | 1530 | 12.35 | 24 | EGYPT | STORE |  | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24 | Maximum | 11.3333 | 215.0775 | 19.6667 | 374.4966 |  | 0.0028571
13 | 6305246 | 2.282 | 4.2 | 0.6 | 0.00 | 2500 | 6350 | CLEAR | 67.9 | 0 | 4.5 |  | 45.8 | 0.38 |  | 6.98 | 7.61 | 6.95 | 16.3 | 16.8 | 18 |  | 8.5 | 0.1 | 0 | 13 | 281 | 5347.9583 | 165 | 3140.2602 | 10 | 190.3188 | 10 | 314 | 5976.0103 | 117 | 2226.73 | 19 | 361.6057
14 | 6307585 | 2.339 | 4 | 0.6 | 0.00 | 1500 | 1000 | CLEAR | 66.6 | 0 |  |  | 47.1 | 0.36 |  | 6.9 | 7.42 | 6.72 | 15.9 | 15.8 | 17.5 |  | 4 | 0.01 | 0 | 14
15 | 6309705 | 2.12 | 5.1 | 0.7 | 0.00 | 0 | 0 | CLOUDY | 66.1 | 0.53 |  |  | 44.1 | 0.45 |  | 6.85 | 7.44 | 6.7 | 15 | 16 | 17.9 |  | 9 | 0.01 | 0 | 15
16 | 6312039 | 2.334 | 4 | 0.7 | 0.00 | 7100 | 5000 | CLEAR | 68.9 | 0.01 |  |  | 46.4 | 0.56 | 60.9 | 6.97 | 8.3 | 6.99 | 15.3 | 16.1 | 17.8 |  | 20 | 0.01 | 0 | 16 | [14 empty] | 78872 | 3 | 4.5 | 34.1 | 32 | 36 | 2295 | 12.36 | 36 | EGYPT | STORE |  | SETTLEABLE
17 | 6314323 | 2.284 | 4.1 | 0.6 | 0.00 | 4900 | 9500 | CLEAR | 69.7 | 0 |  |  | 44.2 | 0.46 | 45.9 | 7.12 | 7.58 | 7.1 | 16.1 | 16.8 | 18.1 |  | 7.5 | 0.1 | 0 | 17 | [26 empty] | SOLIDS | Reporting : | - | - | - | - | 0.0028571 | 0.01 | (mg / L) | 0 | 01/01 | GR
18 | 6316517 | 2.194 | 4 | 0.6 | 0.00 | 1350 | 7500 | RAIN | 65.4 | 0.08 |  |  | 44.4 | 0.46 | 21.3 | 7.08 | 7.96 | 6.89 | 15.4 | 16.4 | 18.1 |  | 7.5 | 1 | 0 | 18 | 259 | 4739.1716 |  |  | 10 | 182.9796 | 10 | 228 | 4171.9349 |  |  | 17 | 311.0653 | [13 empty] | Effluent | Permit : | - | - | - | - | (Report) | 0.3 | (mg / L) | - | 01/01 | GR
19 | 6318756 | 2.239 | 4.4 | 0.7 | 0.00 | 6600 | 10000 | RAIN | 64.3 | 0.59 |  |  | 54.7 | 0.45 |  | 6.91 | 7.26 | 6.75 | 16.5 | 16.4 | 18.1 |  | 7 | 0.1 | 0 | 19 | 298 | 5564.6315 |  |  | 11 | 205.4059 | 11 | 346 | 6460.948 |  |  | 20 | 373.4652 |  | 49254 | 4 | 3 | 21.7 | 30 | 24 | 1530 | 12.38 | 24 | EGYPT | STORE
20 | 6321125 | 2.369 | 5.2 | 0.7 | 0.00 | 4700 | 5000 | CLOUDY | 66.8 | 0.32 |  |  | 57 | 0.62 |  | 6.68 | 7.82 | 6.94 | 16.7 | 16.3 | 17.8 |  | 5 | 0.1 | 0.01 | 20 | 292 | 5769.1783 | 179 | 3536.5853 | 13 | 256.847 | 12 | 300 | 5927.238 | 94 | 1857.2012 | 22 | 434.6641
21 | 6323544 | 2.419 | 4.6 | 0.8 | 0.00 | 0 | 0 | CLEAR | 67.3 | 0.01 |  |  | 56.2 | 0.48 |  | 6.51 | 6.73 | 6.65 | 17.9 | 17.2 | 18.3 |  | 2.5 | 0.01 | 0 | 21
22 | 6326336 | 2.792 | 4 | 0.6 | 0.00 | 0 | 0 | CLEAR | 69.2 | 0 |  |  | 58.5 | 0.48 |  | 6.76 | 6.79 | 6.74 | 15.9 | 16.6 | 18 |  | 3 | 0.1 | 0 | 22 | [26 empty] | FLOW | Reporting : | 2.2744 | 2.792 | (MGD) | - | - | - | - | 0 | 99/99 | RC |  |  |  | CBOD
23 | 6328477 | 2.141 | 3.8 | 0.6 | 0.00 | 7700 | 8450 | CLEAR | 64.4 | 0.2 |  |  | 48.5 | 0.63 | 1 | 7.25 | 7.03 | 6.53 | 17.8 | 17.8 | 18.9 |  | 7 | 0.01 | 0 | 23 | [14 empty] | 60731 | 2 | 4.25 | 27.9 | 34 | 24 | 2677.5 | 12.44 | 24 | EGYPT | STORE |  | Effluent | Permit : | 3.85 | (Report) | (MGD) | - | - | - | - | - | 99/99 | RC
24 | 6330732 | 2.255 | 4.2 | 0.6 | 0.00 | 1200 | 5500 | RAIN | 66.5 | 0.02 |  |  | 49 | 0.48 | 13.5 | 6.75 | 7.21 | 6.76 | 17 | 16.7 | 18.2 |  | 4.5 | 0.01 | 0 | 24 | [41 empty] | % Removal
25 | 6333041 | 2.309 | 4.6 | 0.6 | 0.00 | 5200 | 10000 | CLEAR | 72.4 | 0 |  |  | 56 | 0.54 | 20.1 | 6.75 | 7.15 | 6.53 | 17.4 | 17.2 | 18.8 |  | 4 | 0.01 | 0 | 25 | 262 | 5045.3497 |  |  | 12 | 231.0847 | 11 | 272 | 5237.9203 |  |  | 17 | 327.37
26 | 6335348 | 2.307 | 3.8 | 0.6 | 0.00 | 1900 | 10750 | CLEAR | 74.1 | 0 |  |  | 54.7 | 0.56 |  | 7.11 | 7.1 | 6.51 | 16.9 | 17.2 | 18.7 |  | 8.5 | 0.1 | 0 | 26 | 270 | 5194.9026 |  |  | 11 | 211.6442 | 8 | 290 | 5579.7102 |  |  | 18 | 346.3268 |  | 51372 | 3 | 3.5 | 24.8 | 32 | 24 | 1890 | 12.47 | 24 | EGYPT | STORE | [16 empty] | 96.684
27 | 6337540 | 2.192 | 4.2 | 0.6 | 0.00 | 7600 | 9000 | CLEAR | 74.8 | 0 |  |  | 55.2 | 0.51 |  | 6.82 | 7.28 | 6.76 | 17.7 | 17 | 19.1 |  | 4.5 | 0.01 | 0 | 27 | 292 | 5338.1338 | 176 | 3217.5053 | 10 | 182.8128 | 9 | 320 | 5850.0096 | 90 | 1645.3152 | 13 | 237.6566 | [13 empty] | BOD, 5-day | Reporting : | - | - | - | 96.3579 | - | - | (percent) | 0 | 01/30 | CA
28 | 6339675 | 2.135 | 3.9 | 0.6 | 0.00 | 2000 | 500 | CLOUDY | 71.3 | 0.07 |  |  | 45.1 | 0.55 |  | 6.7 | 7.31 | 6.62 | 15.8 | 16.7 | 18.7 |  | 3 | 0.01 | 0 | 28 | [26 empty] | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
29 | 6341715 | 2.04 | 4 | 0.6 | 0.00 | 0 | 0 | CLOUDY | 72.7 | 0 |  |  | 47.8 | 0.5 |  | 6.71 | 7.26 | 6.73 | 15.8 | 16.8 | 18.6 |  | 3 | 0.01 | 0 | 29
30 | 6343791 | 2.076 | 3.8 | 0.6 | 0.00 | 2500 | 6250 | CLOUDY | 71 | 0 |  |  | 50.1 | 0.57 | 1 | 7 | 7.23 | 6.85 | 16.6 | 17.4 | 19.4 |  | 8.5 | 0.01 | 0 | 30 | [14 empty] | 70348 | 3 | 4.5 | 31 | 33 | 32 | 2295 | 12.39 | 24 | EGYPT | SPREAD
31 | 6345901 | 2.11 | 3.8 | 0.6 | 0.00 | 1200 | 8000 | CLEAR | 74.8 | 0 |  |  | 49.3 | 0.67 | 5 | 7.03 | 7.31 | 6.99 | 16.8 | 17.5 | 19.2 |  | 9 | 0.01 | 0 | 31 | [22 empty] | 8 | EGYPT | STORE
[53 empty] | TSS | Reporting : | - | - | - | 94.2714 | - | - | (percent) | 0 | 01/30 | CA
Total | 70506 | 70.506 | - | - | 0 | 94450 | 169800 | - | - | 3.8 | 4.5 |  | 1396.6 | - | - | - | - | - | - | - | - |  | - | - | - | Total | - | - | - | - | - | - | - | - | - | - | - | - | - |  | 549471 | - | 35.75 | 266.6 | - | 260 | 21127.5 | - | 260 | - | - |  | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
Maximum | - | 2.792 | 7.2 | 0.8 | 0 | 10200 | 11000 | - | 74.8 | 0.87 | - |  | - | 0.67 | 60.9 | 7.25 | 8.3 | 7.1 | 17.9 | 17.8 | 19.4 |  | 20 | 1 | 0.01 | Maximum | 306 | 6050.8868 | 184 | 3536.5853 | 13 | 256.847 | 12 | 408 | 8067.8491 | 117 | 2226.73 | 22 | 434.6641 |  | - | 4 | - | - | 34 | - | - | 12.47 | - | - | -
Minimum | - | 2.04 | 3.8 | 0.6 | 0 | 0 | 0 | - | 59.8 | 0 | - |  | - | 0.36 | 1 | 6.51 | 6.73 | 6.51 | 14.1 | 15 | 16.4 |  | 2.5 | 0.01 | 0 | Minimum | 259 | 4658.8241 | 165 | 3140.2602 | 8 | 141.7133 | 7 | 228 | 4171.9349 | 90 | 1645.3152 | 13 | 237.6566 |  | - | 2 | - | - | 30 | - | - | 12.35 | - | - | -
Average | - | 2.2744 | 4.2645 | 0.64516 | 0.000 | 3046.7742 | 5477.4194 | - | 67.0581 | 0.12258 | - |  | - | - | - | 6.9119 | 7.4968 | 6.7823 | 16.1871 | 16.4774 | 18.0065 |  | 6.629 | 0.065161 | 0.0012903 | Average | 279.5833 | 5295.1133 | 176 | 3340.9977 | 10.1667 | 192.8514 | 9.25 | 315.6667 | 5981.8191 | 100.5 | 1908.4443 | 18.0833 | 343.2765 |  | 61052.3333 | 3.2222 | 3.9722 | 29.6222 | 32.2222 | 28.8889 | 2347.5 | 12.3922 | 23.6364 | - | -
[53 empty] | CHLORINE | Reporting : | - | - | - | - | - | 0.67 | - | 0 | 02/01 | GR
[13 empty] | Geometric Mean : |  | 8.0577 | [14 empty] | Percent Removal : |  | 96.3579 |  |  |  | Percent Removal : |  | 94.2714 | [14 empty] | Effluent | Permit : | - | - | - | - | - | 0.86 | (mg/L) | - | 02/01 | GR

## Graph Jul07
Plant Capacity
3.85 mgd

## August 07
BRUNSWICK SEWER DISTRICT | [11 empty] | State Discharge License Number W 002600-5L-C-R | [9 empty] | Certifying Official: |  |  | Francis E. McVey | BRUNSWICK SEWER DISTRICT | [14 empty] | State Discharge License Number W 002600-5L-C-R | [12 empty] | BRUNSWICK SEWER DISTRICT | [9 empty] | State Discharge License Number W 002600-5L-C-R
Monthly Report of Treatment Operations : |  |  |  |  | August | 2007 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [12 empty] | General Manager | Monthly Report of Treatment Operations : | [5 empty] | August | 2007 | [7 empty] | N.P.D.E.S. Permit Number ME 0100102 | [10 empty] | Page 2. |  | Monthly Report of Treatment Operations : |  |  | August | 2007 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [7 empty] | Page 3.
SETTLEABLE
| FLOW | [6 empty] | WEATHER |  |  |  |  | DISINFECTION |  |  | P.H. |  |  | TEMPERATURE |  |  |  | SOLIDS |  |  |  |  | BIOCHEMICAL OXYGEN DEMAND | [6 empty] | TOTAL SUSPENDED SOLIDS | [6 empty] | SLUDGE DEWATERING | [8 empty] | SLUDGE UTILIZATION |  |  |  | SUMMARY DATA | [11 empty] | HIGH WEEKLY AVERAGE VALUES
|  | Total | Maxim. | Minim. | [8 empty] | Hypo - | [39 empty] | Stored |  |  |  | LOADING |  |  | CONCENTRATION |  |  |  | REPORTING |  |  |  | BOD |  | TSS |  |  | SETTLEABLE SOLIDS
| Totalizer | Flow | Flow | Flow | Flow | Holding | Septic |  | Average | Total | Grit |  | chlorite | Chlorine | [19 empty] | CBOD | [7 empty] | Quantity | Feed | Filter |  | Cake | Sludge | Lime | Average |  | Quantity |  | or |  |  |  | Monthly | Daily |  | Mo Aver | High Wkly | Daily |  |  |  | Sample
Date | Reading | Treated | (instant.) | (instant.) | By-passed | Received | Added | Conditions | Temp. | Precip. | Removed |  | Used | Residual | E. Coli | Influent | Primary | Effluent | Influent | Primary | Effluent |  | Influent | Primary | Effluent | Date |  | Influent | Influent | Primary | Primary | Effluent | Effluent | Effluent | Influent | Influent | Primary | Primary | Effluent | Effluent |  | Dewatered | Solids | Operation | Polymer | Dry Solid | Dewatered | Added | pH |  | Utilized | Site | Spread |  |  |  | Average | Maximum | Units | Minimum | Average | Maximum | Units | Exceptions | Frequency | Type |  | High Weekly Average |  | High Weekly Average |  |  | High Weekly Average
|  | (MG) | (MG) | (MG) | (MG) | (gallons) | (gallons) |  | (deg. F.) | (inches) | (cu. yd.) |  | (gallons) | (mg/L) | (#/100) | (s.u.) | (s.u.) | (s.u.) | (deg. C.) | (deg. C.) | (deg. C.) |  | (ml/L) | (ml/L) | (ml/L) |  |  | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) |  | (gallons) | (%) | (hours) | (lbs) | (%) | (cu. yd.) | (lbs) | (s.u.) |  | (cu. yd.) | [16 empty] | (mg / L) | (lbs / day) | (mg / L) | (lbs / day) |  | (mg / L)
6345901
1 | 6348022 | 2.121 | 3.8 | 0.6 | 0.00 | 1000 | 7000 | CLEAR | 67.9 | 0 |  |  | 51.6 | 0.42 | 1 | 6.9 | 7.45 | 6.87 | 21.7 | 17.4 | 18.9 |  | 4 | 0.01 | 0 | 1 |  | 284 | 5023.7158 |  |  | 9 | 159.2023 | 8 | 300 | 5306.742 |  |  | 19 | 336.0937 | [14 empty] | BOD, 5-day | Reporting : | 208.4351 | 279.3066 | (lbs / day) | 12.2143 | 15 | 17 | (mg / L) | 0 | 03/07 | 24 | Week 1 | 9.5 | 166.0452 | 18.3333 | 319.9224 |  | 0 | check formulas for designation of weeks
2 | 6350104 | 2.082 | 3.9 | 0.6 | 0.00 | 7050 | 8000 | CLEAR | 74.4 | 0 |  |  | 33.7 | 0.57 |  | 7.16 | 7.17 | 6.64 | 16.8 | 18.1 | 19.2 |  | 9 | 0.1 | 0 | 2 | * | 328 | 5695.3526 |  |  |  |  | 7 | 224 | 3889.5091 |  |  | 17 | 295.186 |  | 42697 | 3 | 3 | 21.7 | 31 | 24 | 1530 | 12.33 |  | 24 | EGYPT | STORE |  | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24
3 | 6352177 | 2.073 | 5 | 0.6 | 0.00 | 4000 | 10250 | CLEAR | 75.7 | 0.36 |  |  | 28.3 | 0.49 |  | 7 | 7.4 | 6.78 | 17.9 | 17.6 | 19.2 |  | 4.5 | 0.1 | 0.01 | 3 |  | 299 | 5169.3572 | 176 | 3042.8323 | 10 | 172.8882 | 9 | 344 | 5947.3541 | 100 | 1728.882 | 19 | 328.4876 | [26 empty] | Week 2 | 11 | 197.2021 | 17.3333 | 311.6241 |  | 0 | identifies cell for keyed data entry
4 | 6354518 | 2.341 | 3.8 | 0.6 | 0.00 | 3200 | 1000 | CLOUDY | 73.3 | 0 |  |  | 30.3 | 0.39 |  | 7.06 | 7.82 | 6.87 | 16.6 | 17.7 | 19.4 |  | 6 | 0.01 | 0 | 4
5 | 6356474 | 1.956 | 3.7 | 0.6 | 0.00 | 150 | 0 | CLEAR | 68.8 | 0 |  |  | 27.1 | 0.6 |  | 7.1 | 7.78 | 6.7 | 17.2 | 17.2 | 18.6 |  | 5 | 0.01 | 0 | 5 | [40 empty] | Week 3 | 12.3333 | 217.6573 | 18 | 317.8235 |  | 0.0014286
6 | 6358396 | 1.922 | 5.9 | 0.6 | 0.00 | 4500 | 5500 | CLOUDY | 63.3 | 0.83 |  |  | 25.3 | 0.62 | 21.3 | 7.23 | 6.47 | 6.84 | 18.3 | 18.1 | 19.2 |  | 16 | 0.1 | 0 | 6 | [15 empty] | 50176 | 3 | 3.5 | 24.8 | 33 | 24 | 1785 | 12.42 |  | 24 | EGYPT | STORE |  | pH | Reporting : | - | - | - | 6.45 | - | 7.17 | (s.u.) | 0 | 01/01 | GR
7 | 6360665 | 2.269 | 3.8 | 0.6 | 0.00 | 6500 | 6600 | CLOUDY | 67.2 | 0 |  |  | 29.7 | 0.54 | 1 | 7.13 | 7.54 | 6.98 | 17 | 17.6 | 18.9 |  | 10 | 0.01 | 0 | 7 | [28 empty] | Effluent | Permit : | - | - | - | 6 | - | 8.5 | (s.u.) | - | 01/01 | GR | Week 4 | 15 | 248.0038 | 25.3333 | 418.7041 |  | 0.0028571
8 | 6362729 | 2.064 | 5.4 | 0.6 | 0.00 | 400 | 9000 | RAIN | 68.6 | 0.7 |  |  | 22.7 | 0.58 | 30.1 | 7.1 | 7.06 | 6.67 | 17 | 17.5 | 19.5 |  | 7 | 0.01 | 0 | 8 |  | 157 | 2702.5603 |  |  | 9 | 154.9238 | 9 | 342 | 5887.1059 |  |  | 19 | 327.0614
9 | 6365032 | 2.303 | 4.1 | 0.6 | 0.00 | 1800 | 4750 | CLEAR | 66.6 | 0 |  |  | 26 | 0.49 |  | 7.1 | 7.86 | 6.76 | 16.4 | 17 | 18.3 |  | 6 | 0.1 | 0 | 9 |  | 278 | 5339.5516 |  |  | 10 | 192.0702 | 8 | 320 | 6146.2464 |  |  | 18 | 345.7264 |  | 50680 | 4 | 3.5 | 24.8 | 34 | 24 | 1785 | 12.25 |  | 24 | EGYPT | STORE | [13 empty] | Week 5 | 12.3333 | 199.137 | 24.6667 | 398.2155
10 | 6367127 | 2.095 | 4.6 | 0.6 | 0.00 | 4000 | 7000 | CLOUDY | 63.2 | 0 |  |  | 23.3 | 0.47 |  | 6.98 | 7.16 | 7.1 | 17.2 | 17.3 | 18.6 |  | 5.5 | 0.01 | 0 | 10 |  | 276 | 4822.3548 | 183 | 3197.4309 | 14 | 244.6122 | 12 | 260 | 4542.798 | 100 | 1747.23 | 15 | 262.0845
11 | 6369343 | 2.216 | 3.8 | 0.6 | 0.00 | 0 | 0 | CLEAR | 68.4 | 0 |  |  | 21.9 | 0.48 |  | 6.93 | 7.1 | 6.79 | 16.8 | 17 | 18.4 |  | 5 | 0.01 | 0 | 11 | [28 empty] | TSS | Reporting : | 353.2579 | 564.2427 | (lbs / day) | 20.7333 | 25.3333 | 35 | (mg / L) | 0 | 03/07 | 24
12 | 6371359 | 2.016 | 3.8 | 0.6 | 0.00 | 0 | 0 | CLEAR | 71.6 | 0 |  |  | 22 | 0.5 |  | 7.06 | 7.12 | 6.83 | 17 | 17.1 | 18.2 |  | 4.5 | 0.01 | 0 | 12 | [28 empty] | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24 | Maximum | 15 | 248.0038 | 25.3333 | 418.7041 |  | 0.0028571
13 | 6373201 | 1.842 | 4.4 | 0.6 | 0.00 | 4300 | 4000 | CLOUDY | 68.9 | 0.17 |  |  | 23.3 | 0.52 | 4.1 | 7.18 | 8.29 | 6.95 | 17.2 | 17.9 | 19.1 |  | 10 | 0.01 | 0 | 13
14 | 6375389 | 2.188 | 3.9 | 0.6 | 0.00 | 3200 | 10500 | CLEAR | 64.2 | 0.01 |  |  | 32 | 0.48 | 2 | 7.18 | 8.98 | 6.78 | 16.9 | 17.3 | 17.8 |  | 9 | 0.01 | 0 | 14 | [15 empty] | 55083 | 3 | 3.75 | 27.9 | 33 | 24 | 1912.5 | 12.34
15 | 6377410 | 2.021 | 4.1 | 0.6 | 0.00 | 700 | 10250 | CLEAR | 64.8 | 0.25 |  |  | 24.9 | 0.41 | 613.1 | 7.09 | 7.19 | 7.13 | 18 | 17.8 | 18.9 |  | 14 | 0.01 | 0.01 | 15 |  | 309 | 5208.2383 |  |  | 13 | 219.1168 | 11 | 370 | 6236.4018 |  |  | 18 | 303.3925 | [9 empty] | * | 24 | EGYPT | STORE
16 | 6379486 | 2.076 | 4.6 | 0.6 | 0.00 | 4600 | 6000 | CLEAR | 68.1 | 0.07 |  |  | 26.7 | 0.47 |  | 6.8 | 9.04 | 6.98 | 18 | 17.7 | 19.1 |  | 4 | 0.01 | 0 | 16 |  | 305 | 5280.7212 |  |  | 11 | 190.4522 | 9 | 350 | 6059.844 |  |  | 17 | 294.3353 |  | 54102 | 3 | 3.75 | 24.8 | 31 | 24 | 2025 | 12.38 | * | 24 | EGYPT | STORE |  | SETTLEABLE
17 | 6381731 | 2.245 | 3.9 | 0.6 | 0.00 | 1200 | 5000 | CLEAR | 67.4 | 0.01 |  |  | 25.9 | 0.59 |  | 7.07 | 7.55 | 7.13 | 16.6 | 17.5 | 19 |  | 6.5 | 0.01 | 0 | 17 |  | 291 | 5448.4803 | 180 | 3370.194 | 13 | 243.4029 | 10 | 312 | 5841.6696 | 97 | 1816.1601 | 19 | 355.7427 | [14 empty] | SOLIDS | Reporting : | - | - | - | - | 0.0028571 | 0.01 | (mg / L) | 0 | 01/01 | GR
18 | 6383707 | 1.976 | 3.8 | 0.6 | 0.00 | 1500 | 3000 | LT RAIN | 61.1 | 0.18 |  |  | 25.4 | 0.48 |  | 6.96 | 6.93 | 6.9 | 17 | 17.3 | 18.2 |  | 3 | 0.01 | 0 | 18 | [28 empty] | Effluent | Permit : | - | - | - | - | (Report) | 0.3 | (mg / L) | - | 01/01 | GR
19 | 6385630 | 1.923 | 3.9 | 0.6 | 0.00 | 0 | 0 | CLEAR | 60.9 | 0 |  |  | 27.6 | 0.49 |  | 6.83 | 6.9 | 6.95 | 17.6 | 17.4 | 18.2 |  | 2 | 0.1 | 0 | 19
20 | 6387560 | 1.93 | 3.8 | 0.6 | 0.00 | 2700 | 7750 | CLEAR | 58.4 | 0 |  |  | 34.8 | 0.71 |  | 6.81 | 6.91 | 7.1 | 18.2 | 17 | 17.6 |  | 6.5 | 0.01 | 0 | 20 | [15 empty] | 106038 | 3 | 3.25 | 24.8 | 31 | 24 | 1657.5 | 12.41 | * | 12 | EGYPT | STORE
21 | 6389530 | 1.97 | 3.8 | 0.6 | 0.00 | 2900 | 9500 | CLEAR | 59.2 | 0 |  |  | 28.3 | 0.64 | 16 | 6.9 | 6.94 | 7.17 | 18 | 17.2 | 18 |  | 9 | 0.1 | 0 | 21 | [23 empty] | * | 12 | EGYPT | STORE
22 | 6391549 | 2.019 | 3.8 | 0.6 | 0.00 | 3800 | 12000 | CLEAR | 59.6 | 0.01 |  |  | 32.2 | 0.63 | 9.7 | 7.16 | 9.14 | 7.08 | 16.8 | 17.4 | 17.6 |  | 9 | 0.01 | 0 | 22 |  | 292 | 4916.8303 |  |  | 14 | 235.7384 | 10 | 356 | 5994.4918 |  |  | 23 | 387.2846 | [14 empty] | FLOW | Reporting : | 2.041 | 2.341 | (MGD) | - | - | - | - | 0 | 99/99 | RC |  |  |  | CBOD
23 | 6393510 | 1.961 | 3.6 | 0.6 | 0.00 | 3500 | 9000 | CLOUDY | 63.1 | 0 |  |  | 31.7 | 0.61 | 387.3 | 6.99 | 8.88 | 7.03 | 18.1 | 17.7 | 18.9 |  | 7.5 | 0.01 | 0.01 | 23 |  | 287 | 4693.8104 |  |  | 14 | 228.9664 | 10 | 332 | 5429.7737 |  |  | 26 | 425.2232 |  | 42554 | 4 | 2.75 | 21.7 | 32 | 24 | 1852.5 | 12.43 | * | 24 | EGYPT | STORE |  | Effluent | Permit : | 3.85 | (Report) | (MGD) | - | - | - | - | - | 99/99 | RC
24 | 6395480 | 1.97 | 3.6 | 0.6 | 0.00 | 0 | 10000 | CLOUDY | 67.9 | 0.15 |  |  | 32.7 | 0.53 |  | 6.97 | 7.31 | 7.01 | 17.7 | 17.7 | 19.2 |  | 6 | 0.01 | 0.01 | 24 |  | 285 | 4682.493 | 190 | 3121.662 | 17 | 279.3066 | 15 | 272 | 4468.9056 | 99 | 1626.5502 | 27 | 443.6046 | [29 empty] | % Removal
25 | 6397451 | 1.971 | 3.8 | 0.6 | 0.00 | 4000 | 0 | CLEAR | 74.1 | 0 |  |  | 34.7 | 0.43 |  | 6.78 | 7.73 | 6.87 | 18.6 | 17.8 | 19.4 |  | 4 | 0.1 | 0 | 25
26 | 6399386 | 1.935 | 3.8 | 0.6 | 0.00 | 0 | 0 | CLEAR | 74.9 | 0 |  |  | 32.7 | 0.44 |  | 6.75 | 8.02 | 6.97 | 18.5 | 18 | 19.5 |  | 3 | 0.1 | 0 | 26 | [43 empty] | 96.522
27 | 6401320 | 1.934 | 4.2 | 0.6 | 0.00 | 5075 | 6000 | CLEAR | 68.8 | 0 |  |  | 35.7 | 0.44 | 4.1 | 7.06 | 6.95 | 6.74 | 17.4 | 17.7 | 18.8 |  | 6 | 0.01 | 0 | 27 | [28 empty] | BOD, 5-day | Reporting : | - | - | - | 95.7725 | - | - | (percent) | 0 | 01/30 | CA
28 | 6403363 | 2.043 | 4.2 | 0.6 | 0.00 | 9000 | 9000 | CLEAR | 66.7 | 0 |  |  | 33.7 | 0.6 | 2 | 7.21 | 7.01 | 6.45 | 18.1 | 18.1 | 18.8 |  | 12 | 0.01 | 0 | 28 | [15 empty] | 57014 | 3 | 3.75 | 27.9 | 31 | 24 | 1912.5 | 12.4 |  | 24 | DINGLEYC14 | STORE |  | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
29 | 6405296 | 1.933 | 3.8 | 0.6 | 0.00 | 9900 | 10750 | CLEAR | 66.7 | 0.01 |  |  | 29.7 | 0.48 | 37.3 | 7.03 | 7.47 | 6.83 | 17.2 | 17.6 | 19.3 |  | 9.5 | 0.01 | 0 | 29 |  | 319 | 5142.6692 |  |  | 16 | 257.9395 | 13 | 388 | 6255.0334 |  |  | 35 | 564.2427
30 | 6407228 | 1.932 | 4.6 | 0.6 | 0.00 | 2600 | 13000 | CLEAR | 70.2 | 0.02 |  |  | 23.9 | 0.45 |  | 7.25 | 7.15 | 6.59 | 17.6 | 17.9 | 19.3 |  | 14 | 0.01 | 0 | 30 |  | 275 | 4431.042 |  |  | 10 | 161.1288 | 10 | 342 | 5510.605 |  |  | 19 | 306.1447 |  | 52135 | 4 | 3.75 | 27.9 | 34 | 24 | 1800 | 12.4 |  | 24 | DINGLEYC14 | STORE
31 | 6409172 | 1.944 |  |  | 0.00 | 3200 | 3000 | CLOUDY | 66.1 | 0.02 |  |  | 23.9 | 0.43 |  | 7.08 | 8.58 | 7.07 | 17.9 | 18.2 | 19.7 |  | 5.5 | 0.01 | 0 | 31 |  | 333 | 5398.9157 | 210 | 3404.7216 | 11 | 178.3426 | 10 | 408 | 6614.8877 | 118 | 1913.1293 | 20 | 324.2592
[55 empty] | TSS | Reporting : | - | - | - | 93.6789 | - | - | (percent) | 0 | 01/30 | CA
Total | 63271 | 63.271 | - | - | 0 | 94775 | 187850 | - | - | 2.79 | 0.0 |  | 901.7 | - | - | - | - | - | - | - | - |  | - | - | - | Total |  | - | - | - | - | - | - | - | - | - | - | - | - | - |  | 510479 | - | 31 | 226.3 | - | 216 | 16260 | - |  | 216 | - | - |  | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
Maximum | - | 2.341 | 5.9 | 0.6 | 0 | 9900 | 13000 | - | 75.7 | 0.83 | - |  | - | 0.71 | 613.1 | 7.25 | 9.14 | 7.17 | 21.7 | 18.2 | 19.7 |  | 16 | 0.1 | 0.01 | Maximum |  | 333 | 5695.3526 | 210 | 3404.7216 | 17 | 279.3066 | 15 | 408 | 6614.8877 | 118 | 1913.1293 | 35 | 564.2427 |  | - | 4 | - | - | 34 | - | - | 12.43 |  | - | - | -
Minimum | - | 1.842 | 3.6 | 0.6 | 0 | 0 | 0 | - | 58.4 | 0 | - |  | - | 0.39 | 1 | 6.75 | 6.47 | 6.45 | 16.4 | 17 | 17.6 |  | 2 | 0.01 | 0 | Minimum |  | 157 | 2702.5603 | 176 | 3042.8323 | 9 | 154.9238 | 7 | 224 | 3889.5091 | 97 | 1626.5502 | 15 | 262.0845 |  | - | 3 | - | - | 31 | - | - | 12.25 |  | - | - | -
Average | - | 2.041 | 4.1067 | 0.6 | 0.000 | 3057.2581 | 6059.6774 | - | 67.1 | 0.09 | - |  | - | - | - | 7.0274 | 7.5774 | 6.889 | 17.5903 | 17.5742 | 18.8 |  | 7.1935 | 0.033226 | 0.0012903 | Average |  | 287.8667 | 4930.4062 | 187.8 | 3227.3682 | 12.2143 | 208.4351 | 10.0667 | 328 | 5608.7579 | 102.8 | 1766.3903 | 20.7333 | 353.2579 |  | 56719.8889 | 3.3333 | 3.4444 | 25.1444 | 32.2222 | 24 | 1806.6667 | 12.3733 |  | 21.6 | - | -
[55 empty] | CHLORINE | Reporting : | - | - | - | - | - | 0.71 | - | 0 | 02/01 | GR
[13 empty] | Geometric Mean : |  | 11.4668 | [15 empty] | Percent Removal : |  | 95.7725 |  |  |  | Percent Removal : |  | 93.6789 | [15 empty] | Effluent | Permit : | - | - | - | - | - | 0.86 | (mg/L) | - | 02/01 | GR
[50 empty] | * | Slude delievered to Egypt August 15-23
[27 empty] | * | Eff depleted <2.0mg/L | [22 empty] | moved 8/27 from Egypt to Dingley C-14

## Graph Aug07
Plant Capacity
3.85 mgd

## September 07
BRUNSWICK SEWER DISTRICT | [11 empty] | State Discharge License Number W 002600-5L-C-R | [9 empty] | Certifying Official: |  |  | Francis E. McVey | BRUNSWICK SEWER DISTRICT | [14 empty] | State Discharge License Number W 002600-5L-C-R | [11 empty] | BRUNSWICK SEWER DISTRICT | [9 empty] | State Discharge License Number W 002600-5L-C-R
Monthly Report of Treatment Operations : |  |  |  |  | September | 2007 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [12 empty] | General Manager | Monthly Report of Treatment Operations : | [5 empty] | September | 2007 | [7 empty] | N.P.D.E.S. Permit Number ME 0100102 | [9 empty] | Page 2. |  | Monthly Report of Treatment Operations : |  |  | September | 2007 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [7 empty] | Page 3.
SETTLEABLE
| FLOW | [6 empty] | WEATHER |  |  |  |  | DISINFECTION |  |  | P.H. |  |  | TEMPERATURE |  |  |  | SOLIDS |  |  |  |  | BIOCHEMICAL OXYGEN DEMAND | [6 empty] | TOTAL SUSPENDED SOLIDS | [6 empty] | SLUDGE DEWATERING | [7 empty] | SLUDGE UTILIZATION |  |  |  | SUMMARY DATA | [11 empty] | HIGH WEEKLY AVERAGE VALUES
|  | Total | Maxim. | Minim. | [8 empty] | Hypo - | [38 empty] | Stored |  |  |  | LOADING |  |  | CONCENTRATION |  |  |  | REPORTING |  |  |  | BOD |  | TSS |  |  | SETTLEABLE SOLIDS
| Totalizer | Flow | Flow | Flow | Flow | Holding | Septic |  | Average | Total | Grit |  | chlorite | Chlorine | [19 empty] | CBOD | [7 empty] | Quantity | Feed | Filter |  | Cake | Sludge | Lime | Average | Quantity |  | or |  |  |  | Monthly | Daily |  | Mo Aver | High Wkly | Daily |  |  |  | Sample
Date | Reading | Treated | (instant.) | (instant.) | By-passed | Received | Added | Conditions | Temp. | Precip. | Removed |  | Used | Residual | E. Coli | Influent | Primary | Effluent | Influent | Primary | Effluent |  | Influent | Primary | Effluent | Date |  | Influent | Influent | Primary | Primary | Effluent | Effluent | Effluent | Influent | Influent | Primary | Primary | Effluent | Effluent |  | Dewatered | Solids | Operation | Polymer | Dry Solid | Dewatered | Added | pH | Utilized | Site | Spread |  |  |  | Average | Maximum | Units | Minimum | Average | Maximum | Units | Exceptions | Frequency | Type |  | High Weekly Average |  | High Weekly Average |  |  | High Weekly Average
|  | (MG) | (MG) | (MG) | (MG) | (gallons) | (gallons) |  | (deg. F.) | (inches) | (cu. yd.) |  | (gallons) | (mg/L) | (#/100) | (s.u.) | (s.u.) | (s.u.) | (deg. C.) | (deg. C.) | (deg. C.) |  | (ml/L) | (ml/L) | (ml/L) |  |  | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) |  | (gallons) | (%) | (hours) | (lbs) | (%) | (cu. yd.) | (lbs) | (s.u.) | (cu. yd.) | [16 empty] | (mg / L) | (lbs / day) | (mg / L) | (lbs / day) |  | (mg / L)
6409172
1 | 6411137 | 1.965 | 3.6 | 0.6 | 0.00 | 1300 | 5000 | CLEAR | 64.4 | 0 |  |  | 26.9 | 0.51 |  | 7.09 | 8.12 | 6.82 | 16.8 | 18.2 | 19.3 |  | 9 | 0.01 | 0 | 1 | [27 empty] | BOD, 5-day | Reporting : | 251.9089 | 345.7264 | (lbs / day) | 15 | 18 | 21 | (mg / L) | 0 | 03/07 | 24 | Week 1 | 13.3333 | 217.0402 | 21.3333 | 347.3944 |  | 0 | check formulas for designation of weeks
2 | 6412951 | 1.814 | 3.4 | 0.4 | 0.00 | 0 | 0 | CLEAR | 61.3 | 0 |  |  | 29.7 | 0.49 |  | 7.07 | 8.8 | 6.94 | 16.9 | 18.2 | 18.4 |  | 10 | 0.01 | 0.01 | 2 | [27 empty] | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24
3 | 6414718 | 1.767 | 3.8 | 0.6 | 0.00 | 0 | 0 | CLEAR | 63.7 | 0 |  |  | 33.5 | 0.67 |  | 7.14 | 7.51 | 6.91 | 17.1 | 17.7 | 18.3 |  | 9 | 0.01 | 0.01 | 3 | [39 empty] | Week 2 | 12.6667 | 220.5263 | 22 | 381.6884 |  | 0.0071429 | identifies cell for keyed data entry
4 | 6416619 | 1.901 | 3.8 | 0.5 | 0.00 | 2000 | 6500 | CLEAR | 65 | 0 |  |  | 30.3 | 0.62 | 4.1 | 7.22 | 7.17 | 6.71 | 17.7 | 18.5 | 19.2 |  | 10 | 0.01 | 0 | 4 | [15 empty] | 76758 | 3 | 5.25 | 34.1 | 32 | 36 | 2677.5 | 12.37 | 24 | Dingley C-14 | Store
5 | 6418563 | 1.944 | 4 | 0.5 | 0.00 | 3600 | 10750 | CLEAR | 59.3 | 0 |  |  | 24 | 0.55 | 12 | 7.07 | 8.65 | 7.47 | 16.7 | 17.5 | 18.3 |  | 8 | 0.01 | 0 | 5 |  | 289 | 4685.5454 |  |  | 16 | 259.4074 | 14 | 266 | 4312.6474 |  |  | 22 | 356.6851 | [9 empty] | 12 | Dingley C-14 | Store | [13 empty] | Week 3 | 18 | 308.972 | 23 | 388.4049 |  | 0.0042857
6 | 6420520 | 1.957 | 3.8 | 0.6 | 0.00 | 2500 | 11500 | CLEAR | 58.4 | 0 |  |  | 25.9 | 0.62 | 8.5 | 7.28 | 7.36 | 6.95 | 16.9 | 17.7 | 18.7 |  | 11 | 0.01 | 0.01 | 6 |  | 355 | 5794.0899 |  |  | 11 | 179.5352 | 10 | 380 | 6202.1244 |  |  | 18 | 293.7848 |  | 31429 | 3 | 2.25 | 12.4 | 34 | 12 | 945 | 12.32 | 12 | Dingley C-14 | Store |  | pH | Reporting : | - | - | - | 6.49 | - | 7.47 | (s.u.) | 0 | 01/01 | GR
7 | 6422477 | 1.957 | 3.8 | 0.5 | 0.00 | 1500 | 8250 | CLEAR | 69.2 | 0 |  |  | 26.8 | 0.53 |  | 7.16 | 7.5 | 6.9 | 18 | 18.1 | 19.1 |  | 27 | 0.1 | 0.01 | 7 |  | 375 | 6120.5175 | 187 | 3052.0981 | 13 | 212.1779 | 11 | 362 | 5908.3396 | 100 | 1632.138 | 24 | 391.7131 | [13 empty] | Effluent | Permit : | - | - | - | 6 | - | 8.5 | (s.u.) | - | 01/01 | GR | Week 4 | 17 | 280.1184 | 17.3333 | 287.7328 |  | 0.0042857
8 | 6424428 | 1.951 | 3.6 | 0.6 | 0.00 | 0 | 0 | CLEAR | 73.6 | 0 |  |  | 26.6 | 0.42 |  | 6.94 | 7.62 | 6.63 | 17.5 | 18.2 | 19.8 |  | 2 | 0.01 | 0.01 | 8
9 | 6426278 | 1.85 | 3.6 | 0.6 | 0.00 | 1300 | 2000 | LT RAIN | 62.5 | 0.13 |  |  | 25.4 | 0.4 |  | 7.02 | 7.39 | 6.73 | 17.4 | 17.8 | 19.6 |  | 1 | 0.01 | 0 | 9 | [39 empty] | Week 5 | [5 empty] | 0.002
10 | 6428065 | 1.787 | 4.4 | 0.6 | 0.00 | 7050 | 7250 | LT RAIN | 59.3 | 0.16 |  |  | 24.9 | 0.84 | 1 | 6.73 | 8.63 | 6.85 | 18.6 | 17.8 | 18.9 |  | 6 | 0.01 | 0.01 | 10 | [15 empty] | 54273 | 4 | 3.75 | 27.9 | 34 | 24 | 1912.5 | 12.37 | 24 | Dingley C-14 | Store
11 | 6429968 | 1.903 | 5.6 | 0.4 | 0.00 | 1400 | 10750 | LT RAIN | 59.8 | 1.07 |  |  | 24.1 | 0.58 | 1 | 7.25 | 7.3 | 7.09 | 18.6 | 18.4 | 19.5 |  | 8 | 0.01 | 0 | 11 | [27 empty] | TSS | Reporting : | 351.3051 | 486.3721 | (lbs / day) | 20.9167 | 23 | 28 | (mg / L) | 0 | 03/07 | 24
12 | 6432211 | 2.243 | 3.8 | 0.6 | 0.00 | 7250 | 7500 | CLEAR | 62.5 | 0.01 |  |  | 27.8 | 0.63 | 2 | 7.15 | 7.93 | 6.8 | 18.2 | 18 | 18.1 |  | 9 | 0.01 | 0.01 | 12 |  | 329 | 6154.478 |  |  | 16 | 299.3059 | 14 | 360 | 6734.3832 |  |  | 26 | 486.3721 | [13 empty] | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24 | Maximum | 18 | 308.972 | 23 | 388.4049 |  | 0.0071429
13 | 6434180 | 1.969 | 4 | 0.5 | 0.00 | 8400 | 7750 | CLEAR | 56.6 | 0 |  |  | 24.6 | 0.64 |  | 7.23 | 7.93 | 6.73 | 17.9 | 18.2 | 18.4 |  | 14 | 0.5 | 0 | 13 |  | 356 | 5846.0398 |  |  | 10 | 164.2146 | 10 | 364 | 5977.4114 |  |  | 18 | 295.5863 |  | 51568 | 3 | 3.25 | 24.8 | 34 | 24 | 1560 | 12.4 | 24 | Dingley C-14 | Store
14 | 6436159 | 1.979 | 3.8 | 0.6 | 0.00 | 1000 | 9500 | CLEAR | 58.4 | 0 |  |  | 24.2 | 0.5 |  | 7.34 | 7.07 | 6.91 | 18.1 | 17.8 | 18.6 |  | 11 | 0.01 | 0.01 | 14 |  | 330 | 5446.6038 | 208 | 3433.0109 | 12 | 198.0583 | 10 | 422 | 6965.0509 | 128 | 2112.6221 | 22 | 363.1069
15 | 6438127 | 1.968 | 4.8 | 0.5 | 0.00 | 0 | 4000 | LT RAIN | 58.6 | 0.48 |  |  | 25.4 | 0.66 |  | 6.9 | 6.92 | 6.62 | 18.1 | 18.2 | 19.7 |  | 6 | 0.01 | 0 | 15
16 | 6440189 | 2.062 | 3.8 | 0.5 | 0.00 | 2000 | 1000 | CLEAR | 52.3 | 0 |  |  | 24.9 | 0.44 |  | 6.99 | 7.13 | 6.86 | 18.8 | 18 | 18.5 |  | 5.5 | 0.01 | 0 | 16 | [27 empty] | SETTLEABLE
17 | 6442080 | 1.891 | 4 | 0.6 | 0.00 | 2700 | 9500 | CLEAR | 52.6 | 0 |  |  | 19.5 | 0.46 | <1 | 8.3 | 7.48 | 6.67 | 18.5 | 17.5 | 17.3 |  | 7 | 0.01 | 0 | 17 | [15 empty] | 50749 | 3 | 3.25 | 24.8 | 33 | 24 | 1657.5 | 12.37 | 24 | Dingley C-14 | Store |  | SOLIDS | Reporting : | - | - | - | - | 0.0071429 | 0.01 | (mg / L) | 0 | 01/01 | GR
18 | 6444159 | 2.079 | 4.4 | 0.5 | 0.00 | 3400 | 8000 | CLEAR | 52.4 | 0 |  |  | 22.2 | 0.56 | 11.9 | 7.31 | 7.57 | 7.01 | 20.4 | 20 | 19.7 |  | 13 | 0.01 | 0 | 18 | [27 empty] | Effluent | Permit : | - | - | - | - | (Report) | 0.3 | (mg / L) | - | 01/01 | GR
19 | 6446335 | 2.176 | 3.8 | 0.6 | 0.00 | 2000 | 9000 | CLEAR | 54.3 | 0.01 |  |  | 23.9 | 0.55 | 124.3 | 7.36 | 7.49 | 6.66 | 18.4 | 18.3 | 19.1 |  | 11 | 0.01 | 0.01 | 19 |  | 317 | 5752.8653 |  |  | 15 | 272.2176 | 12 | 320 | 5807.3088 |  |  | 19 | 344.809
20 | 6448294 | 1.959 | 4.2 | 0.5 | 0.00 | 1300 | 13500 | CLOUDY | 61.9 | 0 |  |  | 26.9 | 0.46 |  | 7.2 | 5.81 | 6.49 | 17.8 | 18.9 | 18.8 |  | 10 | 0.8 | 0 | 20 | * | 329 | 5375.2217 | [5 empty] | 448 | 7319.4509 |  |  | 22 | 359.4373 |  | 52091 | 4 | 3.5 | 24.8 | 34 | 24 | 1575 | 12.41 | 12 | Dingley C-14 | Store
21 | 6450268 | 1.974 | 4.4 | 0.5 | 0.00 | 2800 | 6750 | CLEAR | 61.7 | 0 |  |  | 26.2 | 0.32 |  | 7.08 | 8.07 | 6.75 | 17.5 | 17.9 | 19.1 |  | 7.5 | 0.01 | 0.01 | 21 |  | 301 | 4955.4112 |  |  | 21 | 345.7264 | 15 | 404 | 6651.1166 | 119 | 1959.116 | 28 | 460.9685 | [9 empty] | 12 | Hawk Ridge | Compost
22 | 6452460 | 2.192 | 3.8 | 0.5 | 0.00 | 0 | 2000 | CLOUDY | 60.8 | 0 |  |  | 29.4 | 0.6 |  | 7.1 | 7.44 | 6.63 | 18.6 | 18.2 | 19.4 |  | 1 | 0.1 | 0.01 | 22 | [27 empty] | FLOW | Reporting : | 1.9532 | 2.243 | (MGD) | - | - | - | - | 0 | 99/99 | RC |  |  |  | CBOD
23 | 6454314 | 1.854 | 4.4 | 0.5 | 0.00 | 0 | 0 | CLEAR | 64.9 | 0.01 |  |  | 26.9 | 0.41 |  | 6.74 | 8.06 | 6.74 | 18.5 | 18 | 19 |  | 2 | 0.1 | 0 | 23 | [27 empty] | Effluent | Permit : | 3.85 | (Report) | (MGD) | - | - | - | - | - | 99/99 | RC
24 | 6456167 | 1.853 | 4.2 | 0.4 | 0.00 | 5000 | 7000 | CLEAR | 62.8 | 0 |  |  | 23.5 | 0.38 | 2 | 7.21 | 7.29 | 6.97 | 18.2 | 18.3 | 18.5 |  | 8.5 | 0.01 | 0 | 24 | [15 empty] | 49017 | 4 | 3.25 | 24.8 | 28 | 24 |  |  | 24 | Hawk Ridge | Compost | [16 empty] | % Removal
25 | 6458129 | 1.962 | 4 | 0.5 | 0.00 | 0 | 13750 | CLEAR | 65.8 | 0 |  |  | 22.7 | 0.62 | 2 | 7.16 | 7.05 | 6.98 | 17.4 | 18 | 18.2 |  | 8.5 | 0.01 | 0 | 25
26 | 6460047 | 1.918 | 3.8 | 0.4 | 0.00 | 4200 | 8500 | CLEAR | 73.6 | 0 |  |  | 32.2 | 0.46 | 4.1 | 6.91 | 7.51 | 6.85 | 18.8 | 18.7 | 19.9 |  | 11 | 0.4 | 0 | 26 |  | 325 | 5198.739 |  |  | 19 | 303.9263 | 16 | 354 | 5662.6265 |  |  | 17 | 271.934 | [28 empty] | 96.149
27 | 6461948 | 1.901 | 4.5 | 0.5 | 0.00 | 3400 | 11500 | CLOUDY | 67.5 | 0.07 |  |  | 32 | 0.67 |  | 6.98 | 7.02 | 6.63 | 18.9 | 18.5 | 19.4 |  | 6 | 0.01 | 0 | 27 |  | 268 | 4248.9631 |  |  | 16 | 253.6694 | 16 | 358 | 5675.8537 |  |  | 15 | 237.8151 |  | 54016 | 4 | 3.25 | 27.9 | 28 | 24 |  |  | 24 | Hawk Ridge | Compost |  | BOD, 5-day | Reporting : | - | - | - | 95.3242 | - | - | (percent) | 0 | 01/30 | CA
28 | 6464067 | 2.119 | 3.9 | 0.5 | 0.00 | 2000 | 8500 | CLOUDY | 65.9 | 0.2 |  |  | 33.7 | 0.48 |  | 6.93 | 7.2 | 6.93 | 18.5 | 18.3 | 19.6 |  | 7 | 0.01 | 0.01 | 28 |  | 287 | 5071.996 | 184 | 3251.7326 | 16 | 282.7594 | 12 | 296 | 5231.0482 | 98 | 1731.9011 | 20 | 353.4492 | [13 empty] | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
29 | 6465954 | 1.887 | 3.9 | 0.5 | 0.00 | 0 | 4000 | CLEAR | 60.3 | 0 |  |  | 28.3 | 0.36 |  | 7.14 | 7.28 | 6.7 | 16.5 | 17.8 | 17.8 |  | 10 | 0.01 | 0 | 29
30 | 6467768 | 1.814 | 3.9 | 0.5 | 0.00 | 0 | 0 | CLEAR | 50.9 | 0 |  |  | 28.3 | 0.48 |  | 7.21 | 7.14 | 6.91 | 16.7 | 17.6 | 17.4 |  | 10 | 0.01 | 0 | 30
31 | [25 empty] | 31
[54 empty] | TSS | Reporting : | - | - | - | 94.2086 | - | - | (percent) | 0 | 01/30 | CA
Total | 58596 | 58.596 | - | - | 0 | 66100 | 193750 | - | - | 2.14 | 0.0 |  | 800.7 | - | - | - | - | - | - | - | - |  | - | - | - | Total |  | - | - | - | - | - | - | - | - | - | - | - | - | - |  | 419901 | - | 27.75 | 201.5 | - | 192 | 10327.5 | - | 192 | - | - |  | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
Maximum | - | 2.243 | 5.6 | 0.6 | 0 | 8400 | 13750 | - | 73.6 | 1.07 | - |  | - | 0.84 | 124.3 | 8.3 | 8.8 | 7.47 | 20.4 | 20 | 19.9 |  | 27 | 0.8 | 0.01 | Maximum |  | 375 | 6154.478 | 208 | 3433.0109 | 21 | 345.7264 | 16 | 448 | 7319.4509 | 128 | 2112.6221 | 28 | 486.3721 |  | - | 4 | - | - | 34 | - | - | 12.41 | - | - | -
Minimum | - | 1.767 | 3.4 | 0.4 | 0 | 0 | 0 | - | 50.9 | 0 | - |  | - | 0.32 | 1 | 6.73 | 5.81 | 6.49 | 16.5 | 17.5 | 17.3 |  | 1 | 0.01 | 0 | Minimum |  | 268 | 4248.9631 | 184 | 3052.0981 | 10 | 164.2146 | 10 | 266 | 4312.6474 | 98 | 1632.138 | 15 | 237.8151 |  | - | 3 | - | - | 28 | - | - | 12.32 | - | - | -
Average | - | 1.9532 | 4.0267 | 0.52 | 0.000 | 2203.3333 | 6458.3333 | - | 61.3433 | 0.071333 | - |  | - | - | - | 7.1403 | 7.5147 | 6.828 | 17.9333 | 18.1433 | 18.8533 |  | 8.6333 | 0.074667 | 0.004 | Average |  | 321.75 | 5387.5392 | 193 | 3245.6139 | 15 | 251.9089 | 12.7273 | 361.1667 | 6037.2801 | 111.25 | 1858.9443 | 20.9167 | 351.3051 |  | 52487.625 | 3.5 | 3.4688 | 25.1875 | 32.125 | 24 | 1721.25 | 12.3733 | 19.2 | - | -
[54 empty] | CHLORINE | Reporting : | - | - | - | - | - | 0.84 | - | 0 | 02/01 | GR
[13 empty] | Geometric Mean : |  | 4.6163 | [15 empty] | Percent Removal : |  | 95.3242 |  |  |  | Percent Removal : |  | 94.2086 | [14 empty] | Effluent | Permit : | - | - | - | - | - | 0.86 | (mg/L) | - | 02/01 | GR
[27 empty] | * | Eff sample seed depleted

## Graph Sep07
Plant Capacity
3.85 mgd

## October 07
BRUNSWICK SEWER DISTRICT | [11 empty] | State Discharge License Number W 002600-5L-C-R | [9 empty] | Certifying Official: |  |  | Francis E. McVey | BRUNSWICK SEWER DISTRICT | [13 empty] | State Discharge License Number W 002600-5L-C-R | [11 empty] | BRUNSWICK SEWER DISTRICT | [9 empty] | State Discharge License Number W 002600-5L-C-R
Monthly Report of Treatment Operations : |  |  |  |  | October | 2007 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [12 empty] | General Manager | Monthly Report of Treatment Operations : |  |  |  |  | October | 2007 | [7 empty] | N.P.D.E.S. Permit Number ME 0100102 | [9 empty] | Page 2. |  | Monthly Report of Treatment Operations : |  |  | October | 2007 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [7 empty] | Page 3.
SETTLEABLE
| FLOW | [6 empty] | WEATHER |  |  |  |  | DISINFECTION |  |  | P.H. |  |  | TEMPERATURE |  |  |  | SOLIDS |  |  |  | BIOCHEMICAL OXYGEN DEMAND | [6 empty] | TOTAL SUSPENDED SOLIDS | [6 empty] | SLUDGE DEWATERING | [7 empty] | SLUDGE UTILIZATION |  |  |  | SUMMARY DATA | [11 empty] | HIGH WEEKLY AVERAGE VALUES
|  | Total | Maxim. | Minim. | [8 empty] | Hypo - | [37 empty] | Stored |  |  |  | LOADING |  |  | CONCENTRATION |  |  |  | REPORTING |  |  |  | BOD |  | TSS |  |  | SETTLEABLE SOLIDS
| Totalizer | Flow | Flow | Flow | Flow | Holding | Septic |  | Average | Total | Grit |  | chlorite | Chlorine | [18 empty] | CBOD | [7 empty] | Quantity | Feed | Filter |  | Cake | Sludge | Lime | Average | Quantity |  | or |  |  |  | Monthly | Daily |  | Mo Aver | High Wkly | Daily |  |  |  | Sample
Date | Reading | Treated | (instant.) | (instant.) | By-passed | Received | Added | Conditions | Temp. | Precip. | Removed |  | Used | Residual | E. Coli | Influent | Primary | Effluent | Influent | Primary | Effluent |  | Influent | Primary | Effluent | Date | Influent | Influent | Primary | Primary | Effluent | Effluent | Effluent | Influent | Influent | Primary | Primary | Effluent | Effluent |  | Dewatered | Solids | Operation | Polymer | Dry Solid | Dewatered | Added | pH | Utilized | Site | Spread |  |  |  | Average | Maximum | Units | Minimum | Average | Maximum | Units | Exceptions | Frequency | Type |  | High Weekly Average |  | High Weekly Average |  |  | High Weekly Average
|  | (MG) | (MG) | (MG) | (MG) | (gallons) | (gallons) |  | (deg. F.) | (inches) | (cu. yd.) |  | (gallons) | (mg/L) | (#/100) | (s.u.) | (s.u.) | (s.u.) | (deg. C.) | (deg. C.) | (deg. C.) |  | (ml/L) | (ml/L) | (ml/L) |  | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) |  | (gallons) | (%) | (hours) | (lbs) | (%) | (cu. yd.) | (lbs) | (s.u.) | (cu. yd.) | [16 empty] | (mg / L) | (lbs / day) | (mg / L) | (lbs / day) |  | (mg / L)
6467768
1 | 6469631 | 1.863 | 3.9 | 0.6 | 0.00 | 4500 | 9000 | CLOUDY | 53 | 0 | [5 empty] | 7.06 | 6.83 | 6.99 | 17.2 | 17.6 | 17.8 |  | 10 | 0.01 | 0 | 1 | [26 empty] | BOD, 5-day | Reporting : | 270.9255 | 423.5636 | (lbs / day) | 16.4615 | 20.6667 | 27 | (mg / L) | 0 | 03/07 | 24 | Week 1 | 15 | 239.8417 | 23.3333 | 372.4422 |  | 0 | check formulas for designation of weeks
2 | 6471583 | 1.952 | 4.2 | 0.5 | 0.00 | 6350 | 4500 | CLOUDY | 55 | 0 | [5 empty] | 7.03 | 6.81 | 6.65 | 17.6 | 17.6 | 17.5 |  | 5 | 0.1 | 0 | 2 | [26 empty] | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24
3 | 6473515 | 1.932 | 4.2 | 0.5 | 0.00 | 1200 | 12250 | LT RAIN | 60.9 | 0.01 |  |  | O | O | O | 6.75 | 6.77 | 6.37 | 18.5 | 18 | 18.7 |  | 7 | 0.01 | 0 | 3 | 336 | 5413.9277 |  |  | 16 | 257.8061 | 12 | 364 | 5865.0883 |  |  | 18 | 290.0318 | [25 empty] | Week 2 | 20.6667 | 331.2537 | 20 | 321.2401 |  | 0 | identifies cell for keyed data entry
4 | 6475433 | 1.918 | 3.6 | 0.5 | 0.00 | 1200 | 7000 | LT RAIN | 66.1 | 0 | [5 empty] | 7.25 | 5.18 | 6.25 | 17.8 | 18.6 | 17.5 |  | 13 | 4 | 0 | 4 | 357 | 5710.6148 |  |  | 16 | 255.9379 | 13 | 438 | 7006.3006 |  |  | 25 | 399.903 |  | 43967 | 4 | 3.75 | 21.7 | 26 | 24 |  |  | 24 | Old Town | LANDFILL
5 | 6477331 | 1.898 | 4.4 | 0.5 | 0.00 | 750 | 10000 | CLEAR | 60.7 | 0.01 |  |  | F | F | F | 6.76 | 7.07 | 6.61 | 18.7 | 17.9 | 18.7 |  | 10 | 0.01 | 0 | 5 | 359 | 5682.7259 | 214 | 3387.4745 | 13 | 205.7812 | 10 | 394 | 6236.7521 | 116 | 1836.2011 | 27 | 427.3916 | [25 empty] | Week 3 | 15.3333 | 263.2354 | 20.3333 | 349.3876 |  | 0.0057143
6 | 6479333 | 2.002 | 4.2 | 0.5 | 0.00 | 0 | 0 | CLOUDY | 59.8 | 0.35 | [5 empty] | 7.08 | 7.14 | 6.7 | 16.4 | 17.2 | 18.6 |  | 4.5 | 0.01 | 0 | 6 | [26 empty] | pH | Reporting : | - | - | - | 6.25 | - | 7.32 | (s.u.) | 0 | 01/01 | GR
7 | 6481615 | 2.282 | 3.8 | 0.5 | 0.00 | 0 | 0 | CLOUDY | 54.8 | 0.01 |  |  | F | F | F | 6.98 | 7.44 | 6.87 | 18 | 17.5 | 18.3 |  | 5 | 0.01 | 0 | 7 | [26 empty] | Effluent | Permit : | - | - | - | 6 | - | 8.5 | (s.u.) | - | 01/01 | GR | Week 4 | 16 | 272.4845 | 21 | 357.6359 |  | 0
8 | 6483311 | 1.696 | 3.6 | 0.5 | 0.00 | 0 | 2500 | CLOUDY | 50 | 0.02 | [5 empty] | 7.26 | 7.31 | 6.95 | 16.6 | 17.1 | 17.6 |  | 6 | 0.01 | 0 | 8
9 | 6485115 | 1.804 | 3.8 | 0.4 | 0.00 | 0 | 10250 | CLEAR | 53.2 | 0 | [5 empty] | 7.17 | 7.53 | 7.09 | 17.7 | 17.3 | 16.9 |  | 7 | 0.01 | 0 | 9 | [38 empty] | Week 5
10 | 6487036 | 1.921 | 3.6 | 0.5 | 0.00 | 1900 | 8500 | CLEAR | 54.1 | 0.08 | [5 empty] | 6.95 | 7.26 | 7.05 | 18.1 | 17.6 | 17.8 |  | 4 | 0.01 | 0 | 10 | 387 | 6200.1812 |  |  | 14 | 224.296 | 10 | 380 | 6088.0332 |  |  | 18 | 288.3805 |  | 57691 | 4 | 3.5 | 24.8 | 28 | 24 |  |  | 24 | Hawk Ridge | COMPOST
11 | 6488917 | 1.881 | 4 | 0.6 | 0.00 | 2500 | 9000 | LT RAIN | 55.8 | 0.05 |  |  | F | F | F | 7.04 | 7.38 | 7.19 | 17.7 | 17.8 | 18.3 |  | 7.5 | 0.01 | 0 | 11 | 347 | 5443.5764 |  |  | 27 | 423.5636 | 22 | 328 | 5145.5131 |  |  | 21 | 329.4383 |  | 44359 | 5 | 3.75 | 34.1 | 26 | 24 |  |  | 24 | Hawk Ridge | COMPOST |  | TSS | Reporting : | 342.2948 | 427.3916 | (lbs / day) | 20.7692 | 23.3333 | 27 | (mg / L) | 0 | 03/07 | 24
12 | 6490892 | 1.975 | 5.4 | 0.7 | 0.00 | 3300 | 12500 | LT RAIN | 53.8 | 2.44 | [5 empty] | 6.97 | 7.05 | 7.21 | 17.8 | 17.3 | 18 |  | 10 | 0.01 | 0 | 12 | 314 | 5172.051 | 191 | 3146.0565 | 21 | 345.9015 | 15 | 322 | 5303.823 | 108 | 1778.922 | 21 | 345.9015 | [13 empty] | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24 | Maximum | 20.6667 | 331.2537 | 23.3333 | 372.4422 |  | 0.0057143
13 | 6493669 | 2.777 | 4 | 0.6 | 0.00 | 0 | 0 | CLEAR | 47.3 | 0 |  |  | O | O | O | 6.95 | 6.98 | 6.88 | 17 | 16.9 | 16.7 |  | 4 | 0.01 | 0 | 13
14 | 6495769 | 2.1 | 4.6 | 0.6 | 0.00 | 0 | 0 | CLEAR | 47.3 | 0 | [5 empty] | 7.02 | 7.33 | 7.16 | 17.5 | 17.1 | 16.7 |  | 12 | 0.01 | 0 | 14
15 | 6498266 | 2.497 | 4.1 | 0.5 | 0.00 | 2400 | 9000 | CLEAR | 47 | 0 |  |  | R | R | R | 7.19 | 7.77 | 7.21 | 17.4 | 17.4 | 17.1 |  | 6 | 0.01 | 0.01 | 15 | [14 empty] | 55759 | 3 | 3.75 | 40.3 | 27 | 24 |  |  | 24 | Hawk Ridge | COMPOST
16 | 6500347 | 2.081 | 4.2 | 0.6 | 0.00 | 0 | 12250 | CLEAR | 48.6 | 0 | [5 empty] | 7.27 | 7.46 | 7.32 | 17.5 | 17 | 17.1 |  | 9.5 | 0.01 | 0 | 16 | [26 empty] | SETTLEABLE
17 | 6502425 | 2.078 | 3.9 | 0.5 | 0.00 | 1000 | 4750 | CLEAR | 46.4 | 0 | [5 empty] | 7.33 | 7.4 | 6.9 | 17.2 | 16.7 | 16.4 |  | 5 | 0.01 | 0.01 | 17 | 294 | 5095.1729 |  |  | 12 | 207.9662 | 9 | 300 | 5199.156 |  |  | 21 | 363.9409 | [13 empty] | SOLIDS | Reporting : | - | - | - | - | 0.0057143 | 0.01 | (mg / L) | 0 | 01/01 | GR
18 | 6504495 | 2.07 | 3.9 | 0.5 | 0.00 | 1500 | 13000 | CLEAR | 52.2 | 0 | [5 empty] | 7.19 | 5.78 | 6.64 | 17.3 | 16.9 | 16.9 |  | 6 | 0.4 | 0 | 18 | 299 | 5161.8762 |  |  | 15 | 258.957 | 11 | 248 | 4281.4224 |  |  | 17 | 293.4846 |  | 63286 | 3 | 3.75 | 37.2 | 28 | 24 |  |  | 24 | Hawk Ridge | COMPOST |  | Effluent | Permit : | - | - | - | - | (Report) | 0.3 | (mg / L) | - | 01/01 | GR
19 | 6506532 | 2.037 | 5.3 | 0.6 | 0.00 | 5200 | 10000 | CLOUDY | 57.4 | 0.85 |  |  | S | S | S | 7.11 | 7.23 | 6.95 | 17.3 | 17.3 | 17.8 |  | 9 | 0.01 | 0.01 | 19 | 328 | 5572.2542 | 197 | 3346.7503 | 19 | 322.783 | 13 | 378 | 6421.6832 | 115 | 1953.6867 | 23 | 390.7373
20 | 6508839 | 2.307 | 4 | 0.6 | 0.00 | 0 | 0 | CLEAR | 61.3 | 0.26 | [5 empty] | 7.01 | 7.12 | 6.74 | 17 | 17.5 | 18.2 |  | 5 | 0.01 | 0.01 | 20
21 | 6510920 | 2.081 | 3.8 | 0.5 | 0.00 | 0 | 0 | CLEAR | 58.6 | 0 |  |  | E | E | E | 7.1 | 7.42 | 6.5 | 16.8 | 17 | 17.5 |  | 3.5 | 0.01 | 0 | 21
22 | 6512962 | 2.042 | 4.4 | 0.4 | 0.00 | 9500 | 10500 | CLEAR | 59.7 | 0 | [5 empty] | 7.18 | 7.28 | 6.63 | 16.7 | 16.9 | 17.4 |  | 9 | 0.01 | 0 | 22 | [26 empty] | FLOW | Reporting : | 2.0581 | 2.777 | (MGD) | - | - | - | - | 0 | 99/99 | RC |  |  |  | CBOD
23 | 6515044 | 2.082 | 3.8 | 0.6 | 0.00 | 3500 | 8000 | CLEAR | 61.8 | 0 |  |  | A | A | A | 7.23 | 7.14 | 6.57 | 16.9 | 17.6 | 18 |  | 9.5 | 0.01 | 0 | 23 | [14 empty] | 66892 | 2 | 4 | 34.1 | 28 | 24 |  |  | 24 | Hawk Ridge | COMPOST |  | Effluent | Permit : | 3.85 | (Report) | (MGD) | - | - | - | - | - | 99/99 | RC
24 | 6517086 | 2.042 | 3.9 | 0.4 | 0.00 | 600 | 7500 | CLOUDY | 54.3 | 0.01 | [5 empty] | 7.24 | 7.27 | 7.01 | 16.9 | 17.3 | 18 |  | 10 | 0.01 | 0 | 24 | 579 | 9860.5321 |  |  | 16 | 272.4845 | 10 | 792 | 13487.9818 |  |  | 21 | 357.6359 | [28 empty] | % Removal
25 | 6519095 | 2.009 | 3.6 | 0.4 | 0.00 | 5300 | 13000 | CLOUDY | 50.7 | 0 |  |  | S | S | S | 7.25 | 6.27 | 6.59 | 17.1 | 17.5 | 16.1 |  | 9 | 1.5 | 0 | 25 | 291 | 4875.7225 |  |  | 15 | 251.3259 | 10 | 306 | 5127.0484 |  |  | 14 | 234.5708 |  | 59386 | 3 | 4 | 34.1 | 28 | 24 |  |  | 24 | Hawk Ridge | COMPOST
26 | 6520995 | 1.9 | 3.6 | 0.6 | 0.00 | 1750 | 11500 | CLEAR | 45.2 | 0.01 | [5 empty] | 7.16 | 7.35 | 6.95 | 16.6 | 16.9 | 17 |  | 6 | 0.01 | 0 | 26 | 297 | 4706.262 | 195 | 3089.97 | 16 | 253.536 | 10 | 334 | 5292.564 | 103 | 1632.138 | 22 | 348.612 | [28 empty] | 96.3067
27 | 6522881 | 1.886 | 4.8 | 0.6 | 0.00 | 0 | 0 | RAIN | 54.8 | 1.06 |  |  | O | O | O | 7.12 | 7.2 | 6.63 | 15.8 | 16.3 | 16.1 |  | 5 | 0.01 | 0 | 27 | [26 empty] | BOD, 5-day | Reporting : | - | - | - | 95.0825 | - | - | (percent) | 0 | 01/30 | CA
28 | 6525243 | 2.362 | 4.2 | 0.6 | 0.00 | 0 | 0 | CLEAR | 49.7 | 0 | [5 empty] | 7.05 | 7.26 | 6.67 | 15.9 | 16 | 16.4 |  | 8 | 0.01 | 0 | 28 | [26 empty] | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
29 | 6527367 | 2.124 | 4.2 | 0.6 | 0.00 | 4000 | 9750 | CLEAR | 37.2 | 0 |  |  | N | N | N | 7.18 | 7.1 | 6.91 | 16.3 | 16 | 15.5 |  | 5.5 | 0.01 | 0 | 29
30 | 6529499 | 2.132 | 3.7 | 0.6 | 0.00 | 1500 | 9000 | CLEAR | 43.2 | 0 | [5 empty] | 7.05 | 7.39 | 7.05 | 16.4 | 15.8 | 15.3 |  | 5 | 0.01 | 0 | 30 | [14 empty] | 64078 | 3 | 3.75 | 31 | 28 | 24 |  |  | 24 | Hawk Ridge | COMPOST
31 | 6531569 | 2.07 | 3.8 | 0.4 | 0.00 | 750 | 10000 | CLEAR | 47 | 0 | [5 empty] | 7.22 | 7.47 | 6.93 | 16.5 | 15.9 | 15.2 |  | 6.5 | 0.01 | 0.01 | 31 | 158 | 2727.6804 |  |  | 14 | 241.6932 | 9 | 206 | 3556.3428 |  |  | 22 | 379.8036
[53 empty] | TSS | Reporting : | - | - | - | 94.3633 | - | - | (percent) | 0 | 01/30 | CA
Total | 63801 | 63.801 | - | - | 0 | 58700 | 213750 | - | - | 5.16 | 0.0 |  | 0 | - | - | - | - | - | - | - | - |  | - | - | - | Total | - | - | - | - | - | - | - | - | - | - | - | - | - |  | 455418 | - | 30.25 | 257.3 | - | 192 |  | - | 192 | - | - |  | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
Maximum | - | 2.777 | 5.4 | 0.7 | 0 | 9500 | 13000 | - | 66.1 | 2.44 | - |  | - | - | - | 7.33 | 7.77 | 7.32 | 18.7 | 18.6 | 18.7 |  | 13 | 4 | 0.01 | Maximum | 579 | 9860.5321 | 214 | 3387.4745 | 27 | 423.5636 | 22 | 792 | 13487.9818 | 116 | 1953.6867 | 27 | 427.3916 |  | - | 5 | - | - | 28 | - | - |  | - | - | -
Minimum | - | 1.696 | 3.6 | 0.4 | 0 | 0 | 0 | - | 37.2 | 0 | - |  | - | - | - | 6.75 | 5.18 | 6.25 | 15.8 | 15.8 | 15.2 |  | 3.5 | 0.01 | 0 | Minimum | 158 | 2727.6804 | 191 | 3089.97 | 12 | 205.7812 | 9 | 206 | 3556.3428 | 103 | 1632.138 | 14 | 234.5708 |  | - | 2 | - | - | 26 | - | - |  | - | - | -
Average | - | 2.0581 | 4.0806 | 0.53226 | 0.000 | 1893.5484 | 6895.1613 | - | 53.1258 | 0.16645 | - |  | - | - | - | 7.1016 | 7.0965 | 6.8442 | 17.1677 | 17.1452 | 17.2613 |  | 7.1774 | 0.20226 | 0.0016129 | Average | 334.3077 | 5509.429 | 199.25 | 3242.5628 | 16.4615 | 270.9255 | 11.8462 | 368.4615 | 6077.8238 | 110.5 | 1800.237 | 20.7692 | 342.2948 |  | 56927.25 | 3.375 | 3.7812 | 32.1625 | 27.375 | 24 |  |  | 24 | - | -
[13 empty] | Geometric Mean : |  | - | [14 empty] | Percent Removal : |  | 95.0825 |  |  |  | Percent Removal : |  | 94.3633

## Graph Oct07
Plant Capacity
3.85 mgd

## November 07
BRUNSWICK SEWER DISTRICT | [11 empty] | State Discharge License Number W 002600-5L-C-R | [9 empty] | Certifying Official: |  |  | Francis E. McVey | BRUNSWICK SEWER DISTRICT | [14 empty] | State Discharge License Number W 002600-5L-C-R | [11 empty] | BRUNSWICK SEWER DISTRICT | [9 empty] | State Discharge License Number W 002600-5L-C-R
Monthly Report of Treatment Operations : |  |  |  |  | November | 2007 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [12 empty] | General Manager | Monthly Report of Treatment Operations : | [5 empty] | November | 2007 | [7 empty] | N.P.D.E.S. Permit Number ME 0100102 | [9 empty] | Page 2. |  | Monthly Report of Treatment Operations : |  |  | November | 2007 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [7 empty] | Page 3.
SETTLEABLE
| FLOW | [6 empty] | WEATHER |  |  |  |  | DISINFECTION |  |  | P.H. |  |  | TEMPERATURE |  |  |  | SOLIDS |  |  |  |  | BIOCHEMICAL OXYGEN DEMAND | [6 empty] | TOTAL SUSPENDED SOLIDS | [6 empty] | SLUDGE DEWATERING | [7 empty] | SLUDGE UTILIZATION |  |  |  | SUMMARY DATA | [11 empty] | HIGH WEEKLY AVERAGE VALUES
|  | Total | Maxim. | Minim. | [8 empty] | Hypo - | [38 empty] | Stored |  |  |  | LOADING |  |  | CONCENTRATION |  |  |  | REPORTING |  |  |  | BOD |  | TSS |  |  | SETTLEABLE SOLIDS
| Totalizer | Flow | Flow | Flow | Flow | Holding | Septic |  | Average | Total | Grit |  | chlorite | Chlorine | [19 empty] | CBOD | [7 empty] | Quantity | Feed | Filter |  | Cake | Sludge | Lime | Average | Quantity |  | or |  |  |  | Monthly | Daily |  | Mo Aver | High Wkly | Daily |  |  |  | Sample
Date | Reading | Treated | (instant.) | (instant.) | By-passed | Received | Added | Conditions | Temp. | Precip. | Removed |  | Used | Residual | E. Coli | Influent | Primary | Effluent | Influent | Primary | Effluent |  | Influent | Primary | Effluent | Date |  | Influent | Influent | Primary | Primary | Effluent | Effluent | Effluent | Influent | Influent | Primary | Primary | Effluent | Effluent |  | Dewatered | Solids | Operation | Polymer | Dry Solid | Dewatered | Added | pH | Utilized | Site | Spread |  |  |  | Average | Maximum | Units | Minimum | Average | Maximum | Units | Exceptions | Frequency | Type |  | High Weekly Average |  | High Weekly Average |  |  | High Weekly Average
|  | (MG) | (MG) | (MG) | (MG) | (gallons) | (gallons) |  | (deg. F.) | (inches) | (cu. yd.) |  | (gallons) | (mg/L) | (#/100) | (s.u.) | (s.u.) | (s.u.) | (deg. C.) | (deg. C.) | (deg. C.) |  | (ml/L) | (ml/L) | (ml/L) |  |  | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) |  | (gallons) | (%) | (hours) | (lbs) | (%) | (cu. yd.) | (lbs) | (s.u.) | (cu. yd.) | [16 empty] | (mg / L) | (lbs / day) | (mg / L) | (lbs / day) |  | (mg / L)
6531569
1 | 6533606 | 2.037 | 4.1 | 0.4 | 0.00 | 4200 | 5000 | CLEAR | 52.2 | 0 | [5 empty] | 7.28 | 6.74 | 6.6 | 16.5 | 16.5 | 16.5 |  | 10 | 1 | 0 | 1 |  | 467 | 7933.6669 |  |  | 14 | 237.8401 | 8 | 556 | 9445.6505 |  |  | 21 | 356.7602 |  | 60791 | 4 | 3.5 | 31 | 28 | 24 |  |  | 24 | Hawk Ridge | COMPOST |  | BOD, 5-day | Reporting : | 309.8453 | 400.1365 | (lbs / day) | 16.2857 | 20.3333 | 23 | (mg / L) |  | 03/07 | 24 | Week 1 | 14 | 239 | 21 | 358 |  | 0 | check formulas for designation of weeks
2 | 6535635 | 2.029 | 3.9 | 0.6 | 0.00 | 1350 | 11750 | CLEAR | 41.5 | 0 | [5 empty] | 7.21 | 7.36 | 6.96 | 16.3 | 15.8 | 15.4 |  | 7 | 0.01 | 0 | 2 |  | 408 | 6904.1189 | 178 | 3012.0911 | 14 | 236.906 | 9 | 466 | 7885.5868 | 85 | 1438.3581 | 20 | 338.4372 | [13 empty] | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24
3 | 6537666 | 2.031 | 3.9 | 0.6 | 0.00 | 0 | 0 | CLOUDY | 39.6 | 0.91 |  |  | O | O | O | 7.14 | 6.91 | 6.52 | 16.1 | 16 | 15.6 |  | 4 | 0.01 | 0 | 3 | [39 empty] | Week 2 | 16.6667 | 318.727 | 18.3333 | 349.8185 |  | 0 | identifies cell for keyed data entry
4 | 6539867 | 2.201 | 4 | 0.6 | 0.00 | 0 | 0 | CLEAR | 44.6 | 0 | [5 empty] | 7.11 | 7.23 | 6.86 | 15.8 | 15.2 | 15.1 |  | 4 | 0.01 | 0 | 4
5 | 6541926 | 2.059 | 5 | 0.5 | 0.00 | 2000 | 9750 | CLEAR | 40.2 | 0 |  |  | F | F | F | 7.5 | 6.28 | 6.8 | 16.4 | 15.7 | 15.1 |  | 5 | 0.5 | 0 | 5 | [15 empty] | 70528 | 2 | 4 | 37.2 | 28 | 24 |  |  | 24 | Hawk Ridge | COMPOST | [13 empty] | Week 3 | 20.3333 | 377.335 | 20.3333 | 380.3235 |  | 0
6 | 6544046 | 2.12 | 4.6 | 0.6 | 0.00 | 4200 | 13500 | LT RAIN | 46.6 | 0.97 | [5 empty] | 7.27 | 7.38 | 6.99 | 16.2 | 15.8 | 15.5 |  | 12 | 0.01 | 0 | 6 | [27 empty] | pH | Reporting : | - | - | - | 6.52 | - | 7.44 | (s.u.) |  | 01/01 | GR
7 | 6546475 | 2.429 | 4.1 | 0.5 | 0.00 | 200 | 7250 | CLEAR | 38.6 | 0.01 |  |  | F | F | F | 7.25 | 7.41 | 6.91 | 15.9 | 15.2 | 14.7 |  | 8 | 0.01 | 0 | 7 |  | 533 | 10797.4394 |  |  | 18 | 364.6415 | 12 | 360 | 7292.8296 |  |  | 18 | 364.6415 | [13 empty] | Effluent | Permit : | - | - | - | 6 | - | 8.5 | (s.u.) | - | 01/01 | GR | Week 4 | 15.6667 | 301.7023 | 18 | 346.5187 |  | 0.0014286
8 | 6548723 | 2.248 | 4 | 0.6 | 0.00 | 5200 | 6500 | CLOUDY | 35.3 | 0 | [5 empty] | 7.12 | 7.25 | 7.44 | 15.8 | 15.2 | 14.4 |  | 10 | 0.1 | 0 | 8 | * |  |  |  |  | 14 | 262.4765 | 8 | 1840 | 34496.9088 |  |  | 18 | 337.4698 |  | 55439 | 3 | 3.25 | 27.9 | 28 | 23 |  |  | 23 | Hawk Ridge | COMPOST
9 | 6550915 | 2.192 | 4.6 | 0.6 | 0.00 | 6100 | 12750 | CLOUDY | 35.6 | 0 | [5 empty] | 7.15 | 7.21 | 7.2 | 15.5 | 15 | 14.2 |  | 5 | 0.01 | 0 | 9 |  | 521 | 9524.5469 | 188 | 3436.8806 | 18 | 329.063 | 11 | 201 | 3674.5373 | 96 | 1755.0029 | 19 | 347.3443 | [25 empty] | Week 5 | 14 | 289.9318 | 20.3333 | 421.2812
10 | 6553334 | 2.419 | 4 | 0.5 | 0.00 | 0 | 0 | CLEAR | 33.7 | 0 | [5 empty] | 6.75 | 7.04 | 6.9 | 15.8 | 14.8 | 14 |  | 8 | 0.01 | 0 | 10
11 | 6555416 | 2.082 | 3.8 | 0.5 | 0.00 | 0 | 0 | CLEAR | 33 | 0 |  |  | F | F | F | 6.88 | 7.21 | 7.13 | 14.7 | 14.5 | 13.4 |  | 5 | 0.1 | 0 | 11 | [27 empty] | TSS | Reporting : | 370.6445 | 530.1738 | (lbs / day) | 19.4286 | 21 | 26 | (mg / L) |  | 03/07 | 24
12 | 6557441 | 2.025 | 4 | 0.5 | 0.00 | 0 | 2000 | CLEAR | 32.7 | 0 | [5 empty] | 6.84 | 7.2 | 7.19 | 15.1 | 14.4 | 13.6 |  | 6 | 0.01 | 0 | 12 | [27 empty] | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24 | Maximum | 20.3333 | 377.335 | 21 | 421.2812 |  | 0.0014286
13 | 6559536 | 2.095 | 3.8 | 0.5 | 0.00 | 2500 | 10500 | LT RAIN | 41.8 | 0.13 |  |  | O | O | O | 6.91 | 7.26 | 6.95 | 15.4 | 15 | 14.5 |  | 5 | 0.01 | 0 | 13 | [15 empty] | 62266 | 3 | 3.75 | 34.1 | 29 | 23 |  |  | 23 | Hawk Ridge | COMPOST
14 | 6561622 | 2.086 | 3.8 | 0.6 | 0.00 | 2000 | 10250 | CLEAR | 41.6 | 0.01 | [5 empty] | 7.22 | 7.42 | 7.04 | 15.5 | 14.7 | 14.2 |  | 9 | 0.01 | 0 | 14 |  | 363 | 6315.1981 |  |  | 23 | 400.1365 | 15 | 306 | 5323.5554 |  |  | 22 | 382.7393
15 | 6563667 | 2.045 | 3.7 | 0.8 | 0.00 | 8500 | 9500 | CLEAR | 53.1 | 0.47 |  |  | R | R | R | 7.04 | 7.27 | 6.79 | 15 | 15 | 15.2 |  | 7 | 0.01 | 0 | 15 |  | 346 | 5901.1338 |  |  | 20 | 341.106 | 12 | 350 | 5969.355 |  |  | 19 | 324.0507 |  | 32418 | 3 | 2.25 | 15.5 | 29 | 12 |  |  | 12 | Hawk Ridge | COMPOST
16 | 6566270 | 2.603 | 4.3 | 0.6 | 0.00 | 3275 | 12000 | LT RAIN | 38 | 0.89 | [5 empty] | 7.25 | 7.56 | 6.83 | 15.2 | 14.2 | 14.6 |  | 8.5 | 0.1 | 0 | 16 |  | 288 | 6252.1978 | 178 | 3864.2056 | 18 | 390.7624 | 11 | 310 | 6729.7962 | 108 | 2344.5742 | 20 | 434.1804 | [13 empty] | SETTLEABLE
17 | 6568473 | 2.203 | 3.9 | 0.6 | 0.00 | 0 | 2000 | CLEAR | 32.6 | 0 | [5 empty] | 6.86 | 7.35 | 7.16 | 14.3 | 14.2 | 13.7 |  | 3.5 | 0.01 | 0 | 17 | [27 empty] | SOLIDS | Reporting : | - | - | - | - | 0.0014286 | 0.01 | (mg / L) |  | 01/01 | GR
18 | 6570717 | 2.244 | 4.2 | 0.6 | 0.00 | 0 | 0 | CLEAR | 31.1 | 0 | [5 empty] | 6.95 | 7.31 | 6.96 | 14.3 | 14 | 13.4 |  | 5 | 0 | 0 | 18 | [27 empty] | Effluent | Permit : | - | - | - | - | (Report) | 0.3 | (mg / L) | - | 01/01 | GR
19 | 6572989 | 2.272 | 4 | 0.6 | 0.00 | 200 | 5500 | CLEAR | 29.5 | 0 |  |  | S | S | S | 7.13 | 7.4 | 7.08 | 14.8 | 14 | 13.2 |  | 6.5 | 0.01 | 0 | 19 |  | 201 | 3808.6445 |  |  | 12 | 227.3818 | 8 | 156 | 2955.9629 |  |  | 15 | 284.2272 |  | 55165 | 4 | 3.75 | 31 | 29 | 23 |  |  | 23 | Hawk Ridge | COMPOST
20 | 6575320 | 2.331 | 4.2 | 0.6 | 0.00 | 3800 | 7750 | CLEAR | 33.8 | 0.09 | 8 |  |  |  |  | 6.99 | 7.41 | 7.19 | 14.9 | 14.1 | 13.6 |  | 5 | 0.01 | 0.01 | 20 |  | 253 | 4918.4566 |  |  | 18 | 349.9297 | 13 | 216 | 4199.1566 |  |  | 21 | 408.2513
21 | 6577632 | 2.312 | 3.8 | 0.6 | 0.00 | 3250 | 9250 | LT RAIN | 34.5 | 0.07 |  |  | E | E | E | 7.18 | 7.32 | 7.03 | 14.8 | 14.3 | 13.8 |  | 11 | 0.01 | 0 | 21 |  | 273 | 5264.0078 | 150 | 2892.312 | 17 | 327.7954 | 11 | 238 | 4589.135 | 88 | 1696.823 | 18 | 347.0774 |  | 36013 | 4 | 3 | 24.8 | 30 | 19 |  |  | 19 | Hawk Ridge | COMPOST
22 | 6579865 | 2.233 | 4 | 0.6 | 0.00 | 0 | 0 | RAIN | 38.4 | 0.09 | [5 empty] | 6.82 | 7.17 | 7.12 | 14.3 | 13.8 | 13.9 |  | 4 | 0.01 | 0 | 22 | [27 empty] | FLOW | Reporting : | 2.2175 | 2.603 | (MGD) | - | - | - | - |  | 99/99 | RC |  |  |  | CBOD
23 | 6581848 | 1.983 | 3.6 | 0.6 | 0.00 | 0 | 0 | CLOUDY | 32.3 | 0 |  |  | A | A | A | 7.01 | 7.15 | 7.08 | 14.2 | 13.5 | 13.2 |  | 5 | 0.01 | 0 | 23 | [27 empty] | Effluent | Permit : | 3.85 | (Report) | (MGD) | - | - | - | - | - | 99/99 | RC
24 | 6583915 | 2.067 | 3.8 | 0.6 | 0.00 | 0 | 0 | CLEAR | 25.2 | 0 | [5 empty] | 7.16 | 7.24 | 6.92 | 14 | 12.9 | 12.2 |  | 4 | 0.01 | 0 | 24 | [42 empty] | % Removal
25 | 6585975 | 2.06 | 3.8 | 0.6 | 0.00 | 0 | 1500 | CLOUDY | 34 | 0 |  |  | S | S | S | 7.12 | 7.19 | 7.02 | 14.2 | 13.2 | 12.8 |  | 3.5 | 0.01 | 0 | 25
26 | 6588107 | 2.132 | 4 | 0.8 | 0.00 | 3700 | 9500 | CLOUDY | 39.8 | 0.35 | [5 empty] | 7.09 | 7.51 | 7.2 | 14.2 | 13.9 | 13.3 |  | 7.5 | 0.01 | 0 | 26 | [15 empty] | 70746 | 3 | 4.75 | 37.2 | 27 | 22 |  |  | 22 | Hawk Ridge | COMPOST | [16 empty] | 96.8755
27 | 6590624 | 2.517 | 4.2 | 0.7 | 0.00 | 2500 | 7750 | CLOUDY | 41.6 | 0.67 |  |  | O | O | O | 7 | 7.28 | 7.05 | 14.3 | 13.5 | 14.7 |  | 5.5 | 0.1 | 0 | 27 | [27 empty] | BOD, 5-day | Reporting : | - | - | - | 94.9494 | - | - | (percent) |  | 01/30 | CA
28 | 6593122 | 2.498 | 4.4 | 0.8 | 0.00 | 2000 | 6000 | CLEAR | 33.7 | 0 | [5 empty] | 6.85 | 7.68 | 7.05 | 14 | 13.4 | 12.8 |  | 5.5 | 0.01 | 0 | 28 |  | 193 | 4020.8308 |  |  | 13 | 270.8332 | 8 | 240 | 4999.9968 |  |  | 17 | 354.1664 | [13 empty] | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
29 | 6595650 | 2.528 | 4.3 | 0.6 | 0.00 | 1200 | 9750 | CLEAR | 36.6 | 0.01 |  |  | N | N | N | 7.07 | 7.48 | 6.95 | 14.3 | 13.5 | 12.9 |  | 6 | 0.1 | 0 | 29 |  | 172 | 3626.3654 |  |  | 11 | 231.9187 | 7 | 218 | 4596.2074 |  |  | 18 | 379.5034 |  | 32685 | 3 | 2.75 | 18.6 | 28 | 12 |  |  | 12 | Hawk Ridge | COMPOST
30 | 6598095 | 2.445 | 9.4 | 0.6 | 0.00 | 1000 | 8000 | CLEAR | 34.6 | 0.01 | [5 empty] | 7.03 | 7.32 | 7.24 | 14 | 13.5 | 13.1 |  | 7 | 0.01 | 0 | 30 |  | 220 | 4486.086 | 135 | 2752.8255 | 18 | 367.0434 | 12 | 336 | 6851.4768 | 103 | 2100.3039 | 26 | 530.1738
31 | [25 empty] | 31
[54 empty] | TSS | Reporting : | - | - | - | 95.3047 | - | - | (percent) |  | 01/30 | CA
Total | 66526 | 66.526 | - | - | 0 | 57175 | 177750 | - | - | 4.68 | 8 |  | 0 | - | - | - | - | - | - | - | - |  | - | - | - | Total |  | - | - | - | - | - | - | - | - | - | - | - | - | - |  | 476051 | - | 31 | 257.3 | - | 182 |  | - | 182 | - | - |  | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
Maximum | - | 2.603 | 9.4 | 0.8 | 0 | 8500 | 13500 | - | 53.1 | 0.97 | - |  | - | - | - | 7.5 | 7.68 | 7.44 | 16.5 | 16.5 | 16.5 |  | 12 | 1 | 0.01 | Maximum |  | 533 | 10797.4394 | 188 | 3864.2056 | 23 | 400.1365 | 15 | 1840 | 34496.9088 | 108 | 2344.5742 | 26 | 530.1738 |  | - | 4 | - | - | 30 | - | - |  | - | - | -
Minimum | - | 1.983 | 3.6 | 0.4 | 0 | 0 | 0 | - | 25.2 | 0 | - |  | - | - | - | 6.75 | 6.28 | 6.52 | 14 | 12.9 | 12.2 |  | 3.5 | 0 | 0 | Minimum |  | 172 | 3626.3654 | 135 | 2752.8255 | 11 | 227.3818 | 7 | 156 | 2955.9629 | 85 | 1438.3581 | 15 | 284.2272 |  | - | 2 | - | - | 27 | - | - |  | - | - | -
Average | - | 2.2175 | 4.24 | 0.59667 | 0.000 | 1905.8333 | 5925 | - | 37.5267 | 0.156 | - |  | - | - | - | 7.0727 | 7.2513 | 7.0053 | 15.06 | 14.4933 | 14.0867 |  | 6.4167 | 0.074 | 0.00033333 | Average |  | 326 | 6134.8225 | 165.8 | 3191.663 | 16.2857 | 309.8453 | 10.3571 | 413.7857 | 7786.4396 | 96 | 1867.0124 | 19.4286 | 370.6445 |  | 52894.5556 | 3.2222 | 3.4444 | 28.5889 | 28.4444 | 20.2222 |  |  | 20.2222 | - | -
[13 empty] | Geometric Mean : |  | - | [11 empty] | * | Inf BOD depleted to <1 mg/L |  |  | Percent Removal : |  | 94.9494 |  |  |  | Percent Removal : |  | 95.3047

## Graph Nov07
Plant Capacity
3.85 mgd

## December 07
BRUNSWICK SEWER DISTRICT | [11 empty] | State Discharge License Number W 002600-5L-C-R | [9 empty] | Certifying Official: |  |  | Francis E. McVey | BRUNSWICK SEWER DISTRICT | [13 empty] | State Discharge License Number W 002600-5L-C-R | [11 empty] | BRUNSWICK SEWER DISTRICT | [9 empty] | State Discharge License Number W 002600-5L-C-R
Monthly Report of Treatment Operations : |  |  |  |  | December | 2007 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [12 empty] | General Manager | Monthly Report of Treatment Operations : |  |  |  |  | December | 2007 | [7 empty] | N.P.D.E.S. Permit Number ME 0100102 | [9 empty] | Page 2. |  | Monthly Report of Treatment Operations : |  |  | December | 2007 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [7 empty] | Page 3.
SETTLEABLE
| FLOW | [6 empty] | WEATHER |  |  |  |  | DISINFECTION |  |  | P.H. |  |  | TEMPERATURE |  |  |  | SOLIDS |  |  |  | BIOCHEMICAL OXYGEN DEMAND | [6 empty] | TOTAL SUSPENDED SOLIDS | [6 empty] | SLUDGE DEWATERING | [7 empty] | SLUDGE UTILIZATION |  |  |  | SUMMARY DATA | [11 empty] | HIGH WEEKLY AVERAGE VALUES
|  | Total | Maxim. | Minim. | [8 empty] | Hypo - | [37 empty] | Stored |  |  |  | LOADING |  |  | CONCENTRATION |  |  |  | REPORTING |  |  |  | BOD |  | TSS |  |  | SETTLEABLE SOLIDS
| Totalizer | Flow | Flow | Flow | Flow | Holding | Septic |  | Average | Total | Grit |  | chlorite | Chlorine | [18 empty] | CBOD | [7 empty] | Quantity | Feed | Filter |  | Cake | Sludge | Lime | Average | Quantity |  | or |  |  |  | Monthly | Daily |  | Mo Aver | High Wkly | Daily |  |  |  | Sample
Date | Reading | Treated | (instant.) | (instant.) | By-passed | Received | Added | Conditions | Temp. | Precip. | Removed |  | Used | Residual | E. Coli | Influent | Primary | Effluent | Influent | Primary | Effluent |  | Influent | Primary | Effluent | Date | Influent | Influent | Primary | Primary | Effluent | Effluent | Effluent | Influent | Influent | Primary | Primary | Effluent | Effluent |  | Dewatered | Solids | Operation | Polymer | Dry Solid | Dewatered | Added | pH | Utilized | Site | Spread |  |  |  | Average | Maximum | Units | Minimum | Average | Maximum | Units | Exceptions | Frequency | Type |  | High Weekly Average |  | High Weekly Average |  |  | High Weekly Average
|  | (MG) | (MG) | (MG) | (MG) | (gallons) | (gallons) |  | (deg. F.) | (inches) | (cu. yd.) |  | (gallons) | (mg/L) | (#/100) | (s.u.) | (s.u.) | (s.u.) | (deg. C.) | (deg. C.) | (deg. C.) |  | (ml/L) | (ml/L) | (ml/L) |  | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) |  | (gallons) | (%) | (hours) | (lbs) | (%) | (cu. yd.) | (lbs) | (s.u.) | (cu. yd.) | [16 empty] | (mg / L) | (lbs / day) | (mg / L) | (lbs / day) |  | (mg / L)
6598095
1 | 6600400 | 2.305 | 4 | 0.6 | 0.00 | 1200 | 2000 | CLEAR | 22.8 | 0 | [5 empty] | 6.85 | 7.38 | 6.94 | 13.5 | 9 | 8.3 |  | 4.5 | 0.01 | 0 | 1 | [26 empty] | BOD, 5-day | Reporting : | 294.8565 | 420.6613 | (lbs / day) | 17.0833 | 17.6667 | 23 | (mg / L) | 0 | 03/07 | 24 | Week 1 | 17.6667 | 320.3227 | 20.6667 | 374.7245 |  | 0 | check formulas for designation of weeks
2 | 6602646 | 2.246 | 4 | 0.6 | 0.00 | 0 | 0 | CLOUDY | 25 | 0 | [5 empty] | 6.98 | 7.39 | 7.12 | 13.7 | 12 | 8.9 |  | 8 | 0.01 | 0 | 2 | [26 empty] | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24
3 | 6604891 | 2.245 | 3.9 | 0.6 | 0.00 | 0 | 0 | SNOW | 26.2 | 0 |  |  | O | O | O | 6.74 | 6.54 | 6.91 | 13.4 | 13.2 | 11.4 |  | 3.5 | 0.4 | 0 | 3 | [14 empty] | 33360 | 4 | 2.75 | 18.6 | 28 | 12 | [18 empty] | Week 2 | 16 | 279.9821 | 22 | 385.3692 |  | 0 | identifies cell for keyed data entry
4 | 6607232 | 2.341 | 3.8 | 0.6 | 0.00 | 5200 | 6000 | CLOUDY | 25.1 | 0 | [5 empty] | 6.81 | 7.43 | 7.21 | 13.9 | 12.5 | 11.1 |  | 9 | 0.1 | 0 | 4 | [22 empty] | 12 | HAWK RIDGE | COMPOST
5 | 6609308 | 2.076 | 4 | 0.6 | 0.00 | 400 | 5000 | CLEAR | 25.3 | 0.17 |  |  | F | F | F | 7 | 7.5 | 7.06 | 13.7 | 12.8 | 11.2 |  | 7 | 0.1 | 0 | 5 | 217 | 3757.1033 |  |  | 15 | 259.7076 | 11 | 192 | 3324.2573 |  |  | 19 | 328.963 | [25 empty] | Week 3 | 17.3333 | 284.3523 | 19.3333 | 316.6309 |  | 0
6 | 6611551 | 2.243 | 3.8 | 0.6 | 0.00 | 1200 | 6500 | CLEAR | 20.2 | 0.05 | [5 empty] | 7.3 | 8.09 | 7.59 | 13.7 | 12.8 | 11.5 |  | 7 | 0.01 | 0 | 6 | 204 | 3816.1505 |  |  | 15 | 280.5993 | 11 | 184 | 3442.0181 |  |  | 21 | 392.839 |  | 62532 | 4 | 4.5 | 27.9 | 33 | 24 | 2160 | 12.41 | 24 | EGYPT | STORE |  | pH | Reporting : | - | - | - | 6.14 | - | 7.59 | (s.u.) | 0 | 01/01 | GR
7 | 6613744 | 2.193 | 4 | 0.6 | 0.00 | 1500 | 2000 | CLEAR | 20.7 | 0 |  |  | F | F | F | 7.08 | 7.25 | 7.24 | 13.4 | 12.5 | 12.1 |  | 10 | 0.01 | 0 | 7 | 254 | 4645.5635 | 199 | 3639.6344 | 23 | 420.6613 | 15 | 220 | 4023.7164 | 81 | 1481.4592 | 22 | 402.3716 | [13 empty] | Effluent | Permit : | - | - | - | 6 | - | 8.5 | (s.u.) | - | 01/01 | GR | Week 4 | 17.3333 | 294.769 | 20.6667 | 348.4341 |  | 0
8 | 6615877 | 2.133 | 3.8 | 0.6 | 0.00 | 3900 | 0 | CLEAR | 26.6 | 0.17 | [5 empty] | 6.68 | 6.92 | 6.95 | 14.2 | 13.2 | 12.2 |  | 5 | 0.01 | 0 | 8
9 | 6617952 | 2.075 | 3.8 | 0.6 | 0.00 | 0 | 0 | CLEAR | 25.7 | 0 | [5 empty] | 6.77 | 7.04 | 7.09 | 13.7 | 13 | 12.4 |  | 3.5 | 0.01 | 0 | 9 | [38 empty] | Week 5 | [5 empty] | 0.0014286
10 | 6620056 | 2.104 | 3.6 | 0.5 | 0.00 | 2600 | 1000 | LT SNOW | 22 | 0.05 | [5 empty] | 7.08 | 7.42 | 7.12 | 13.6 | 12 | 10.4 |  | 7 | 0.4 | 0 | 10 | [14 empty] | 52231 | 4 | 3.5 | 27.9 | 31 | 24 | 1680 | 12.36 | 24 | EGYPT | STORE
11 | 6622129 | 2.073 | 3.7 | 0.5 | 0.00 | 4900 | 0 | CLEAR | 21.7 | 0.01 |  |  | F | F | F | 7.36 | 7.48 | 7.39 | 13.5 | 12.2 | 10.7 |  | 10 | 0.2 | 0 | 11 | [26 empty] | TSS | Reporting : | 356.2897 | 461.2187 | (lbs / day) | 20.6667 | 22 | 26 | (mg / L) | 0 | 03/07 | 24
12 | 6624215 | 2.086 | 3.7 | 0.4 | 0.00 | 5125 | 4750 | CLEAR | 33.7 | 0.21 | [5 empty] | 7.18 | 7.33 | 6.86 | 13.7 | 12.9 | 12.1 |  | 10 | 0.01 | 0 | 12 | 226 | 3931.7762 |  |  | 17 | 295.7531 | 13 | 232 | 4036.1597 |  |  | 25 | 434.931 | [13 empty] | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24 | Maximum | 17.6667 | 320.3227 | 22 | 385.3692 |  | 0.0014286
13 | 6626293 | 2.078 | 3.9 | 0.4 | 0.00 | 200 | 3000 | CLEAR | 17.1 | 0 |  |  | O | O | O | 7.32 | 6.79 | 7.13 | 13.3 | 12.4 | 11.2 |  | 10 | 0.5 | 0 | 13 | 271 | 4696.5709 |  |  | 14 | 242.6273 | 9 | 402 | 6966.869 |  |  | 15 | 259.9578 |  | 50402 | 4 | 3.75 | 27.9 | 33 | 24 | 1800 | 12.33 | 24 | EGYPT | STORE
14 | 6628420 | 2.127 | 3.6 | 0.5 | 0.00 | 1500 | 2000 | SNOW | 23.5 | 0.11 | [5 empty] | 6.86 | 6.99 | 6.78 | 12.8 | 11.9 | 10.3 |  | 9.5 | 0 | 0 | 14 | 220 | 3902.6196 | 161 | 2856.008 | 17 | 301.5661 | 13 | 278 | 4931.492 | 100 | 1773.918 | 26 | 461.2187
15 | 6630414 | 1.994 | 4 | 0.4 | 0.00 | 0 | 0 | CLEAR | 16 | 0 |  |  | R | R | R | 6.97 | 7.32 | 6.58 | 12.8 | 12 | 11 |  | 4 | 0.1 | 0 | 15
16 | 6632389 | 1.975 | 3.7 | 0.4 | 0.00 | 0 | 0 | SNOW | 13.6 | 0 | [5 empty] | 6.96 | 7.27 | 6.59 | 12.8 | 11.9 | 10.7 |  | 5 | 0.01 | 0 | 16 | [26 empty] | SETTLEABLE
17 | 6634305 | 1.916 | 3.6 | 0.5 | 0.00 | 500 | 0 | CLEAR | 19.1 | 0 | [5 empty] | 6.88 | 7.15 | 6.95 | 12.6 | 11.3 | 7.2 |  | 6.5 | 0.01 | 0 | 17 | 278 | 4442.2843 |  |  | 18 | 287.6299 | 14 | 164 | 2620.6282 |  |  | 17 | 271.6505 |  | 47235 | 4 | 3.25 | 24.8 | 31 | 24 | 1657.5 | 12.43 | 24 | EGYPT | STORE |  | SOLIDS | Reporting : | - | - | - | - | 0.0014286 | 0.01 | (mg / L) | 0 | 01/01 | GR
18 | 6636330 | 2.025 | 3.8 | 0.5 | 0.00 | 2000 | 1000 | CLEAR | 17 | 0.07 | [5 empty] | 6.92 | 7.48 | 7.05 | 12.6 | 12.4 | 10.8 |  | 11 | 0.01 | 0 | 18 | 283 | 4779.4455 |  |  | 21 | 354.6585 | 14 | 250 | 4222.125 |  |  | 20 | 337.77 | [13 empty] | Effluent | Permit : | - | - | - | - | (Report) | 0.3 | (mg / L) | - | 01/01 | GR
19 | 6638274 | 1.944 | 3.6 | 0.6 | 0.00 | 1800 | 2500 | CLEAR | 18.2 | 0.01 |  |  | S | S | S | 6.98 | 7.22 | 6.83 | 12.8 | 11.6 | 10.1 |  | 13 | 0.01 | 0 | 19 | 199 | 3226.379 | 116 | 1880.7034 | 13 | 210.7685 | 9 | 268 | 4345.0733 | 95 | 1540.2312 | 21 | 340.4722
20 | 6640271 | 1.997 | 3.8 | 0.4 | 0.00 | 2000 | 0 | SNOW | 22.3 | 0 | [5 empty] | 7.03 | 7.22 | 6.55 | 13.2 | 12.1 | 10.7 |  | 9 | 0.01 | 0 | 20 | [14 empty] | 39995 | 5 | 2.75 | 21.7 | 32 | 22 | 1402.5 | 12.43 | 22 | EGYPT | STORE
21 | 6642191 | 1.92 | 3.6 | 0.4 | 0.00 | 1700 | 3000 | CLEAR | 17.4 | 0.17 |  |  | E | E | E | 6.99 | 7.03 | 6.76 | 12.8 | 12.1 | 10.2 |  | 6.5 | 0.01 | 0 | 21
22 | 6644083 | 1.892 | 3.6 | 0.5 | 0.00 | 0 | 0 | CLOUDY | 18.2 | 0 | [5 empty] | 6.9 | 7.15 | 6.61 | 12.4 | 11 | 9.2 |  | 3.5 | 0.01 | 0 | 22 | [26 empty] | FLOW | Reporting : | 2.096 | 2.423 | (MGD) | - | - | - | - | 0 | 99/99 | RC |  |  |  | CBOD
23 | 6645903 | 1.82 | 3.7 | 0.6 | 0.00 | 0 | 0 | CLOUDY | 37.7 | 0.83 |  |  | A | A | A | 6.83 | 7.15 | 7.07 | 12.1 | 10.7 | 11.3 |  | 4.5 | 0.01 | 0 | 23 | [26 empty] | Effluent | Permit : | 3.85 | (Report) | (MGD) | - | - | - | - | - | 99/99 | RC
24 | 6648144 | 2.241 | 4 | 0.6 | 0.00 | 500 | 1500 | CLEAR | 39.8 | 0.28 | [5 empty] | 6.94 | 7.44 | 6.62 | 11.2 | 10.1 | 11.6 |  | 5 | 0.01 | 0 | 24 | [41 empty] | % Removal
25 | 6650343 | 2.199 | 3.6 | 0.6 | 0.00 | 0 | 0 | CLEAR | 35.4 | 0 |  |  | S | S | S | 6.72 | 7.15 | 7.02 | 11.7 | 10.3 | 10.4 |  | 2 | 0.01 | 0 | 25
26 | 6652232 | 1.889 | 3.8 | 0.6 | 0.00 | 0 | 3000 | CLEAR | 27.7 | 0 | [5 empty] | 6.78 | 7.11 | 6.95 | 11.5 | 10.9 | 10.4 |  | 15 | 0.1 | 0.01 | 26 | 220 | 3465.9372 |  |  | 14 | 220.5596 | 9 | 142 | 2237.1049 |  |  | 22 | 346.5937 |  | 69335 | 3 | 5 | 37.2 | 34 | 32 | 2400 | 12.36 | 24 | EGYPT | STORE | [16 empty] | 94.695
27 | 6654359 | 2.127 | 3.8 | 0.6 | 0.00 | 0 | 4250 | CLOUDY | 30.6 | 0.02 |  |  | O | O | O | 6.79 | 7.14 | 7.19 | 12.2 | 10.8 | 10.7 |  | 5 | 0.01 | 0 | 27 | 269 | 4771.8394 |  |  | 18 | 319.3052 | 13 | 226 | 4009.0547 |  |  | 19 | 337.0444 | [9 empty] | 8 | EGYPT | STORE |  | BOD, 5-day | Reporting : | - | - | - | 92.894 | - | - | (percent) | 0 | 01/30 | CA
28 | 6656424 | 2.065 | 3.6 | 0.6 | 0.00 | 3200 | 1500 | CLEAR | 31.1 | 0.24 | [5 empty] | 7.29 | 7.34 | 7.1 | 11.9 | 10.5 | 10.3 |  | 8.5 | 0.01 | 0 | 28 | 253 | 4357.1913 | 173 | 2979.4233 | 20 | 344.442 | 20 | 242 | 4167.7482 | 97 | 1670.5437 | 21 | 361.6641 | [13 empty] | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
29 | 6658506 | 2.082 | 4.2 | 0.6 | 0.00 | 0 | 0 | RAIN | 35.8 | 0.45 |  |  | N | N | N | 6.69 | 7.26 | 6.86 | 10.9 | 11 | 11.3 |  | 3 | 0.01 | 0 | 29
30 | 6660929 | 2.423 | 3.8 | 0.6 | 0.00 | 0 | 0 | CLEAR | 33.2 | 0 | [5 empty] | 6.82 | 7.16 | 7.04 | 11.4 | 10.9 | 10.7 |  | 4.5 | 0.01 | 0 | 30
31 | 6663072 | 2.143 | 3.8 | 0.6 | 0.00 | 0 | 0 | SNOW | 28.6 | 0.03 | [5 empty] | 7 | 7 | 6.14 | 11.8 | 11.6 | 10.7 |  | 8.5 | 0.01 | 0 | 31 | [14 empty] | 57283 | 2 | 3.5 | 24.8 | 35 | 12 | 1575 | 12.42 | 12 | EGYPT | STORE
[53 empty] | TSS | Reporting : | - | - | - | 91.1429 | - | - | (percent) | 0 | 01/30 | CA
Total | 64977 | 64.977 | - | - | 0 | 39425 | 49000 | - | - | 2.87 | 0.0 |  | 0 | - | - | - | - | - | - | - | - |  | - | - | - | Total | - | - | - | - | - | - | - | - | - | - | - | - | - |  | 412373 | - | 29 | 210.8 | - | 174 | 12675 | - | 174 | - | - |  | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
Maximum | - | 2.423 | 4.2 | 0.6 | 0 | 5200 | 6500 | - | 39.8 | 0.83 | - |  | - | - | - | 7.36 | 8.09 | 7.59 | 14.2 | 13.2 | 12.4 |  | 15 | 0.5 | 0.01 | Maximum | 283 | 4779.4455 | 199 | 3639.6344 | 23 | 420.6613 | 20 | 402 | 6966.869 | 100 | 1773.918 | 26 | 461.2187 |  | - | 5 | - | - | 35 | - | - | 12.43 | - | - | -
Minimum | - | 1.82 | 3.6 | 0.4 | 0 | 0 | 0 | - | 13.6 | 0 | - |  | - | - | - | 6.68 | 6.54 | 6.14 | 10.9 | 9 | 7.2 |  | 2 | 0 | 0 | Minimum | 199 | 3226.379 | 116 | 1880.7034 | 13 | 210.7685 | 9 | 142 | 2237.1049 | 81 | 1481.4592 | 15 | 259.9578 |  | - | 2 | - | - | 28 | - | - | 12.33 | - | - | -
Average | - | 2.096 | 3.7935 | 0.54194 | 0.000 | 1271.7742 | 1580.6452 | - | 25.0742 | 0.092581 | - |  | - | - | - | 6.9516 | 7.2303 | 6.9452 | 12.8 | 11.729 | 10.6806 |  | 7.0484 | 0.068387 | 0.00032258 | Average | 241.1667 | 4149.4051 | 162.25 | 2838.9423 | 17.0833 | 294.8565 | 12.5833 | 233.3333 | 4027.1872 | 93.25 | 1616.538 | 20.6667 | 356.2897 |  | 51546.625 | 3.75 | 3.625 | 26.35 | 32.125 | 21.75 | 1810.7143 | 12.3914 | 19.3333 | - | -
[13 empty] | Geometric Mean : |  | - | [14 empty] | Percent Removal : |  | 92.894 |  |  |  | Percent Removal : |  | 91.1429

## Graph Dec07
Plant Capacity
3.85 mgd

## ANNUAL 07
BRUNSWICK SEWER DISTRICT | [9 empty] | State Discharge License Number W 002600-5L-C-R | [11 empty] | Gregory H. Thulen
Monthly Report of Treatment Operations : | [23 empty] | 0 | 0 | 0 | 0
Annual Report of Treatment Operations: 2007. | [9 empty] | N.P.D.E.S. Permit Number ME 0100102 | [11 empty] | Treatment Operations Division Supervisor
'file:///tmp/in/input.xls'#$ANNUAL 07 | [21 empty] | Page 1.
[17 empty] | Range | Range | A N N U A L |  |  | P E R M I T
| Parameter |  | Function | Units | JANUARY | FEBRUARY | MARCH | APRIL | MAY | JUNE | JULY | AUGUST | SEPTEMBER | OCTOBER | NOVEMBER | DECEMBER | Maximum | Minimum | Total | Max/Avg/Min | Units | Limits
| PLANT FLOW |  | total | (mg) | 89.288 | 64.677 | 80.808 | 131.244 | 107.058 | 88.168 | 70.506 | 63.271 | 58.596 | 63.801 | 66.526 | 64.977 | 131.244 | 58.596 | 948.92 | 79.0767 | (mg) |  | total; average
|  |  | maximum | (mgd) | 3.583 | 2.715 | 3.53 | 9.77 | 4.383 | 3.759 | 2.792 | 2.341 | 2.243 | 2.777 | 2.603 | 2.423 | 9.77 | 2.243 | - | 9.77 | (mgd) | Report only. | max
|  |  | average | (mgd) | 2.8803 | 2.3099 | 2.6067 | 4.3748 | 3.4535 | 2.9389 | 2.2744 | 2.041 | 1.9532 | 2.0581 | 2.2175 | 2.096 | 4.3748 | 1.9532 | - | 2.6004 | (mgd) | 3.85 | average
|  |  | minimum | (mgd) | 2.488 | 2.122 | 1.999 | 2.992 | 2.832 | 2.452 | 2.04 | 1.842 | 1.767 | 1.696 | 1.983 | 1.82 | 2.992 | 1.696 | - | 1.696 | (mgd) |  | min
| HOLDING WASTE |  | total received | (gallons) | 30850 | 24450 | 35300 | 47050 | 82100 | 78300 | 94450 | 94775 | 66100 | 58700 | 57175 | 39425 | 94775 | 24450 | 708675 | 59056.25 | (gallons) |  | total; average
| SEPTIC WASTE |  | total received | (gallons) | 72500 | 36250 | 66750 | 103150 | 194900 | 200400 | 169800 | 187850 | 193750 | 213750 | 177750 | 49000 | 213750 | 36250 | 1665850 | 138820.8333 | (gallons) |  | total; average
| GRIT |  | total removed | (cubic yards) | 0.0 | 5 | 0.0 | 0.0 | 0.0 | 0.0 | 4.5 | 0.0 | 0.0 | 0.0 | 8 | 0.0 | 8 | 4.5 | 17.5 | 5.8333 | (cubic yards) |  | total; per month
| DISINFECTION |  | hypochlorite | (gallons) | 0 | 0 | 0 | 0 | 572.8 | 894.3 | 1396.6 | 901.7 | 800.7 | 0 | 0 | 0 | 1396.6 | 572.8 | 4566.1 | 913.22 | (gallons) |  | total; average
| pH | Influent | maximum | (std units) | 7.44 | 7.61 | 7.44 | 6.94 | 6.82 | 7.28 | 7.25 | 7.25 | 8.3 | 7.33 | 7.5 | 7.36 | 8.3 | 6.82 | - | 8.3 |  |  | max
|  |  | average |  | 7.0419 | 7.2236 | 6.9574 | 6.5627 | 6.4903 | 6.7917 | 6.9119 | 7.0274 | 7.1403 | 7.1016 | 7.0727 | 6.9516 | 7.2236 | 6.4903 | - | 6.9394 | (std units) |  | average
|  |  | minimum |  | 6.76 | 7.03 | 6.46 | 6.05 | 6.07 | 6.36 | 6.51 | 6.75 | 6.73 | 6.75 | 6.75 | 6.68 | 7.03 | 6.05 | - | 6.05 |  |  | min
|  | Primary | maximum | (std units) | 7.18 | 7.32 | 7.27 | 6.94 | 6.76 | 7.83 | 8.3 | 9.14 | 8.8 | 7.77 | 7.68 | 8.09 | 9.14 | 6.76 | - | - |  |  | max
|  |  | average |  | 7.0168 | 7.1689 | 6.96 | 6.6177 | 6.5213 | 6.8133 | 7.4968 | 7.5774 | 7.5147 | 7.0965 | 7.2513 | 7.2303 | 7.5774 | 6.5213 | - | 7.1054 | (std units) |  | average
|  |  | minimum |  | 6.86 | 7.06 | 6.38 | 6.14 | 6.18 | 6.43 | 6.73 | 6.47 | 5.81 | 5.18 | 6.28 | 6.54 | 7.06 | 5.18 | - | - |  |  | min
|  | Effluent | maximum | (std units) | 7.15 | 7.19 | 6.89 | 6.91 | 6.68 | 7.02 | 7.1 | 7.17 | 7.47 | 7.32 | 7.44 | 7.59 | 7.59 | 6.68 | - | 7.59 |  | 9 | max
|  |  | average |  | 6.8739 | 6.7382 | 6.5345 | 6.6347 | 6.4426 | 6.391 | 6.7823 | 6.889 | 6.828 | 6.8442 | 7.0053 | 6.9452 | 7.0053 | 6.391 | - | 6.7424 | (std units) |  | average
|  |  | minimum |  | 6.39 | 6.35 | 6.04 | 6.16 | 6.21 | 6.07 | 6.51 | 6.45 | 6.49 | 6.25 | 6.52 | 6.14 | 6.52 | 6.04 | - | 6.04 |  | 6 | min
TEMPERATURE
|  | Influent | maximum | (degrees C.) | 12.5 | 12.8 | 11.9 | 11.1 | 15 | 16.5 | 17.9 | 21.7 | 20.4 | 18.7 | 16.5 | 14.2 | 21.7 | 11.1 | - | 21.7 |  |  | max
|  |  | average |  | 11.9065 | 11.2429 | 10.3935 | 10.15 | 12.3323 | 14.4933 | 16.1871 | 17.5903 | 17.9333 | 17.1677 | 15.06 | 12.8 | 17.9333 | 10.15 | - | 13.9381 | (degrees C.) |  | average
|  |  | minimum |  | 11.3 | 10.1 | 9.5 | 8.7 | 10.6 | 13 | 14.1 | 16.4 | 16.5 | 15.8 | 14 | 10.9 | 16.5 | 8.7 | - | 8.7 |  |  | min
|  | Primary | maximum | (degrees C.) | 11.9 | 11.7 | 11.9 | 11.3 | 14.9 | 16.6 | 17.8 | 18.2 | 20 | 18.6 | 16.5 | 13.2 | 20 | 11.3 | - | - |  |  | max
|  |  | average |  | 10.6613 | 10.2214 | 10.1774 | 9.83 | 12.1806 | 14.6233 | 16.4774 | 17.5742 | 18.1433 | 17.1452 | 14.4933 | 11.729 | 18.1433 | 9.83 | - | 13.6047 | (degrees C.) |  | average
|  |  | minimum |  | 7.4 | 8.4 | 6.1 | 8.5 | 10.5 | 13.4 | 15 | 17 | 17.5 | 15.8 | 12.9 | 9 | 17.5 | 6.1 | - | - |  |  | min
|  | Effluent | maximum | (degrees C.) | 12.6 | 10.9 | 11.6 | 12.1 | 16.1 | 18.1 | 19.4 | 19.7 | 19.9 | 18.7 | 16.5 | 12.4 | 19.9 | 10.9 | - | 19.9 |  |  | max
|  |  | average |  | 10.3258 | 9.2571 | 9.8129 | 10.4167 | 13.1935 | 15.91 | 18.0065 | 18.8 | 18.8533 | 17.2613 | 14.0867 | 10.6806 | 18.8533 | 9.2571 | - | 13.8837 | (degrees C.) |  | average
|  |  | minimum |  | 6.9 | 5.6 | 6 | 8.3 | 11.4 | 13.8 | 16.4 | 17.6 | 17.3 | 15.2 | 12.2 | 7.2 | 17.6 | 5.6 | - | 5.6 |  |  | min
SETTLEABLE SOLIDS
|  | Influent | maximum | (ml / l) | 10 | 13 | 17 | 11 | 16 | 10 | 20 | 16 | 27 | 13 | 12 | 15 | 27 | 10 | - | 27 |  |  | max
|  |  | average |  | 4.7258 | 6.2643 | 6.1129 | 3.88 | 5.129 | 5.2667 | 6.629 | 7.1935 | 8.6333 | 7.1774 | 6.4167 | 7.0484 | 8.6333 | 3.88 | - | 6.2064 | (ml / l) |  | average
|  |  | minimum |  | 1.5 | 1.4 | 2.5 | 0.9 | 1.5 | 1 | 2.5 | 2 | 1 | 3.5 | 3.5 | 2 | 3.5 | 0.9 | - | 0.9 |  |  | min
|  | Primary | maximum | (ml / l) | 0.3 | 0.1 | 0.1 | 0.4 | 0.6 | 1 | 1 | 0.1 | 0.8 | 4 | 1 | 0.5 | 4 | 0.1 | - | - |  |  | max
|  |  | average |  | 0.033548 | 0.034643 | 0.027097 | 0.056667 | 0.07 | 0.11533 | 0.065161 | 0.033226 | 0.074667 | 0.20226 | 0.074 | 0.068387 | 0.20226 | 0.027097 | - | 0.071249 | (ml / l) |  | average
|  |  | minimum |  | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0 | 0.01 | 0 | - | - |  |  | min
|  | Effluent | maximum | (ml / l) | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | - | 0.01 |  | 0.3 | max
|  |  | average |  | 0.00064516 | 0.0025 | 0.0025806 | 0.0023333 | 0.0025806 | 0.0026667 | 0.0012903 | 0.0012903 | 0.004 | 0.0016129 | 0.00033333 | 0.00032258 | 0.004 | 0.00032258 | - | 0.0018463 | (ml / l) |  | average
|  |  | minimum |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0 |  |  | min
BRUNSWICK SEWER DISTRICT |  |  |  |  | JUNE: State Discharge License Number W 002600-5L-C-R | [5 empty] | Gregory H. Thulen
Annual Report of Treatment Operations: 2007. |  |  |  |  | JUNE: N.P.D.E.S. Permit Number ME 0100102 | [5 empty] | Treatment Operations Division Supervisor
'file:///tmp/in/input.xls'#$ANNUAL 07 | [21 empty] | Page 2.
[17 empty] | Range | Range | A N N U A L |  |  | P E R M I T
| Parameter |  | Function | Units | JANUARY | FEBRUARY | MARCH | APRIL | MAY | JUNE | JULY | AUGUST | SEPTEMBER | OCTOBER | NOVEMBER | DECEMBER | Maximum | Minimum | Total | Max/Avg/Min | Units | Limits
BIOCHEMICAL OXYGEN DEMAND
|  | Influent | maximum | (mg / l) | 256 | 326 | 329 | 212 | 243 | 293 | 306 | 333 | 375 | 579 | 533 | 283 | 579 | 212 | - | 579 |  |  | max
|  |  | average |  | 216 | 270.5833 | 240.5714 | 167.3333 | 200.8571 | 236.6154 | 279.5833 | 287.8667 | 321.75 | 334.3077 | 326 | 241.1667 | 334.3077 | 167.3333 | - | 260.2196 | (mg / l) |  | average
|  |  | minimum |  | 177 | 218 | 181 | 76 | 150 | 190 | 259 | 157 | 268 | 158 | 172 | 199 | 268 | 76 | - | 76 |  |  | min
|  | Influent | maximum | (pounds) | 5961.7656 | 6135.4795 | 6101.4106 | 15285.0516 | 6879.7327 | 7736.7928 | 6050.8868 | 5695.3526 | 6154.478 | 9860.5321 | 10797.4394 | 4779.4455 | 15285.0516 | 4779.4455 | - | 15285.0516 |  |  | max
|  |  | average |  | 5250.8666 | 5284.2963 | 5102.7027 | 5980.7975 | 5794.1096 | 5808.4212 | 5295.1133 | 4930.4062 | 5387.5392 | 5509.429 | 6134.8225 | 4149.4051 | 6134.8225 | 4149.4051 | - | 5385.6591 | (pounds) |  | average
|  |  | minimum |  | 4582.3213 | 4304.9912 | 3905.18 | 4655.855 | 4912.727 | 4733.784 | 4658.8241 | 2702.5603 | 4248.9631 | 2727.6804 | 3626.3654 | 3226.379 | 4912.727 | 2702.5603 | - | 2702.5603 |  |  | min
|  | Primary | maximum | (mg / l) | 154 | 176 | 193 | 113 | 118 | 162 | 184 | 210 | 208 | 214 | 188 | 199 | 214 | 113 | - | - |  |  | max
|  |  | average |  | 127.75 | 164 | 145 | 100.5 | 113.75 | 143.6 | 176 | 187.8 | 193 | 199.25 | 165.8 | 162.25 | 199.25 | 100.5 | - | 156.5583 | (mg / l) |  | average
|  |  | minimum |  | 101 | 149 | 113 | 84 | 111 | 127 | 165 | 176 | 184 | 191 | 135 | 116 | 191 | 84 | - | - |  |  | min
|  | Primary | maximum | (pounds) | 3491.124 | 3470.5742 | 3441.3676 | 4472.375 | 3707.964 | 3798.5698 | 3536.5853 | 3404.7216 | 3433.0109 | 3387.4745 | 3864.2056 | 3639.6344 | 4472.375 | 3387.4745 | - | - |  |  | max
|  |  | average |  | 3115.9908 | 3147.8288 | 3079.6034 | 3443.6235 | 3296.4225 | 3482.7189 | 3340.9977 | 3227.3682 | 3245.6139 | 3242.5628 | 3191.663 | 2838.9423 | 3482.7189 | 2838.9423 | - | 3221.1113 | (pounds) |  | average
|  |  | minimum |  | 2628.1008 | 2737.58 | 2821.6055 | 2570.1878 | 2967.9224 | 3113.9892 | 3140.2602 | 3042.8323 | 3052.0981 | 3089.97 | 2752.8255 | 1880.7034 | 3140.2602 | 1880.7034 | - | - |  |  | min
|  | Effluent | maximum | (mg / l) | 16 | 17 | 26 | 14 | 17 | 18 | 13 | 17 | 21 | 27 | 23 | 23 | 27 | 13 | - | 27 |  | 50 | max
|  |  | average |  | 13.4615 | 14.4167 | 15.3571 | 11.5833 | 11.5714 | 13.1538 | 10.1667 | 12.2143 | 15 | 16.4615 | 16.2857 | 17.0833 | 17.0833 | 10.1667 | - | 13.8963 | (mg / l) | 30 | average
|  |  | minimum |  | 10 | 10 | 12 | 9 | 10 | 10 | 8 | 9 | 10 | 12 | 11 | 13 | 13 | 8 | - | 8 |  |  | min
|  | Effluent | maximum | (pounds) | 432.8794 | 374.0156 | 579.1796 | 1009.3902 | 490.9841 | 437.85 | 256.847 | 279.3066 | 345.7264 | 423.5636 | 400.1365 | 420.6613 | 1009.3902 | 256.847 | - | 1009.3902 |  | 1605 | max
|  |  | average |  | 329.3235 | 284.7102 | 330.9241 | 440.024 | 336.8752 | 327.8428 | 192.8514 | 208.4351 | 251.9089 | 270.9255 | 309.8453 | 294.8565 | 440.024 | 192.8514 | - | 298.2102 | (pounds) | 963 | average
|  |  | minimum |  | 264.4114 | 177.8922 | 223.1284 | 253.0356 | 236.1888 | 215.0886 | 141.7133 | 154.9238 | 164.2146 | 205.7812 | 227.3818 | 210.7685 | 264.4114 | 141.7133 | - | 141.7133 |  |  | min
|  | Effluent | removal | (percent) | 93.7282 | 94.6121 | 93.5147 | 92.6427 | 94.1859 | 94.3557 | 96.3579 | 95.7725 | 95.3242 | 95.0825 | 94.9494 | 92.894 | 96.3579 | 92.6427 | - | 94.4517 | (percent) | 85 | average
| CBOD | Effluent | maximum | (mg / l) | 13 | 14 | 19 | 12 | 14 | 15 | 12 | 15 | 16 | 22 | 15 | 20 | 22 | 12 | - | 22 |  |  | max
|  |  | average |  | 11.3846 | 12.1667 | 12.7857 | 9.5 | 10.0714 | 11.3077 | 9.25 | 10.0667 | 12.7273 | 11.8462 | 10.3571 | 12.5833 | 12.7857 | 9.25 | - | 11.1706 | (mg / l) |  | average
|  |  | minimum |  | 9 | 9 | 10 | 8 | 8 | 9 | 7 | 7 | 10 | 9 | 7 | 9 | 10 | 7 | - | 7 |  |  | min
|  | Effluent | removal | (percent) | 94.7881 | 95.5613 | 94.5488 | 94.2004 | 94.99 | 95.2249 | 96.684 | 96.522 | 96.149 | 96.3067 | 96.8755 | 94.695 | 96.8755 | 94.2004 | - | 95.5455 | (percent) |  | average
TOTAL SUSPENDED SOLIDS
|  | Influent | maximum | (mg / l) | 256 | 362 | 374 | 362 | 332 | 430 | 408 | 408 | 448 | 792 | 1840 | 402 | 1840 | 256 | - | 1840 |  |  | max
|  |  | average |  | 211 | 281.1667 | 248.2857 | 175.5833 | 251.2857 | 338.3077 | 315.6667 | 328 | 361.1667 | 368.4615 | 413.7857 | 233.3333 | 413.7857 | 175.5833 | - | 293.8369 | (mg / l) |  | average
|  |  | minimum |  | 167 | 196 | 164 | 79 | 136 | 274 | 228 | 224 | 266 | 206 | 156 | 142 | 274 | 79 | - | 79 |  |  | min
|  | Influent | maximum | (pounds) | 6333.1958 | 7097.8571 | 9338.765 | 14047.7792 | 10075.9543 | 10604.3934 | 8067.8491 | 6614.8877 | 7319.4509 | 13487.9818 | 34496.9088 | 6966.869 | 34496.9088 | 6333.1958 | - | 34496.9088 |  |  | max
|  |  | average |  | 5138.1386 | 5493.1368 | 5432.763 | 6083.3475 | 7228.577 | 8305.2491 | 5981.8191 | 5608.7579 | 6037.2801 | 6077.8238 | 7786.4396 | 4027.1872 | 8305.2491 | 4027.1872 | - | 6100.0433 | (pounds) |  | average
|  |  | minimum |  | 3845.4656 | 4296.9014 | 3538.3951 | 3842.8051 | 4763.808 | 6073.1046 | 4171.9349 | 3889.5091 | 4312.6474 | 3556.3428 | 2955.9629 | 2237.1049 | 6073.1046 | 2237.1049 | - | 2237.1049 |  |  | min
|  | Primary | maximum | (mg / l) | 81 | 84 | 93 | 59 | 88 | 121 | 117 | 118 | 128 | 116 | 108 | 100 | 128 | 59 | - | - |  |  | max
|  |  | average |  | 68.25 | 75.5 | 75.4 | 50.5 | 80 | 103.4 | 100.5 | 102.8 | 111.25 | 110.5 | 96 | 93.25 | 111.25 | 50.5 | - | 88.9458 | (mg / l) |  | average
|  |  | minimum |  | 59 | 66 | 51 | 38 | 69 | 90 | 90 | 97 | 98 | 103 | 85 | 81 | 103 | 38 | - | - |  |  | min
|  | Primary | maximum | (pounds) | 1933.5456 | 1511.1079 | 1897.717 | 2768.6131 | 2556.9773 | 2928.5243 | 2226.73 | 1913.1293 | 2112.6221 | 1953.6867 | 2344.5742 | 1773.918 | 2928.5243 | 1511.1079 | - | - |  |  | max
|  |  | average |  | 1671.1317 | 1440.5724 | 1618.7006 | 1801.5943 | 2307.7572 | 2507.9581 | 1908.4443 | 1766.3903 | 1858.9443 | 1800.237 | 1867.0124 | 1616.538 | 2507.9581 | 1440.5724 | - | 1847.1067 | (pounds) |  | average
|  |  | minimum |  | 1404.6311 | 1363.4399 | 1389.1604 | 995.4457 | 2112.3052 | 2132.4546 | 1645.3152 | 1626.5502 | 1632.138 | 1632.138 | 1438.3581 | 1481.4592 | 2132.4546 | 995.4457 | - | - |  |  | min
|  | Effluent | maximum | (mg / l) | 24 | 26 | 37 | 23 | 26 | 39 | 22 | 35 | 28 | 27 | 26 | 26 | 39 | 22 | - | 39 |  | 50 | max
|  |  | average |  | 18.9231 | 21.9167 | 19.8571 | 13.6667 | 20 | 28.3846 | 18.0833 | 20.7333 | 20.9167 | 20.7692 | 19.4286 | 20.6667 | 28.3846 | 13.6667 | - | 20.2788 | (mg / l) | 30 | average
|  |  | minimum |  | 14 | 19 | 12 | 11 | 10 | 20 | 13 | 15 | 15 | 14 | 15 | 15 | 20 | 10 | - | 10 |  |  | min
|  | Effluent | maximum | (pounds) | 649.319 | 537.1127 | 824.2172 | 1658.2839 | 699.309 | 943.9045 | 434.6641 | 564.2427 | 486.3721 | 427.3916 | 530.1738 | 461.2187 | 1658.2839 | 427.3916 | - | 1658.2839 |  | 1605 | max
|  |  | average |  | 461.0166 | 430.1765 | 421.3851 | 550.2287 | 571.2983 | 708.6941 | 343.2765 | 353.2579 | 351.3051 | 342.2948 | 370.6445 | 356.2897 | 708.6941 | 342.2948 | - | 438.3223 | (pounds) | 963 | average
|  |  | minimum |  | 373.3651 | 347.5028 | 205.9646 | 289.4397 | 350.28 | 418.8348 | 237.6566 | 262.0845 | 237.8151 | 234.5708 | 284.2272 | 259.9578 | 418.8348 | 205.9646 | - | 205.9646 |  |  | min
|  | Effluent | removal | (percent) | 91.0317 | 92.2051 | 92.0023 | 92.2164 | 92.0409 | 91.6098 | 94.2714 | 93.6789 | 94.2086 | 94.3633 | 95.3047 | 91.1429 | 95.3047 | 91.0317 | - | 92.8397 | (percent) | 85 | average
BRUNSWICK SEWER DISTRICT |  |  |  |  | JUNE: State Discharge License Number W 002600-5L-C-R | [5 empty] | Gregory H. Thulen
Annual Report of Treatment Operations: 2007. |  |  |  |  | JUNE: N.P.D.E.S. Permit Number ME 0100102 | [5 empty] | Treatment Operations Division Supervisor
'file:///tmp/in/input.xls'#$ANNUAL 07 | [21 empty] | Page 3.
[17 empty] | Range | Range | A N N U A L |  |  | P E R M I T
| Parameter |  | Function | Units | JANUARY | FEBRUARY | MARCH | APRIL | MAY | JUNE | JULY | AUGUST | SEPTEMBER | OCTOBER | NOVEMBER | DECEMBER | Maximum | Minimum | Total | Max/Avg/Min | Units | Limits
SLUDGE DEWATERING
|  | Dewatered | total volume | (gallons) | 341926 | 300492 | 397799 | 401907 | 366000 | 461009 | 549471 | 510479 | 419901 | 455418 | 476051 | 412373 | 549471 | 300492 | 5092826 | - | (gallons) |  | total
|  |  | monthly average | (gallons) | 42740.75 | 37561.5 | 44199.8889 | 44656.3333 | 40666.6667 | 57626.125 | 61052.3333 | 56719.8889 | 52487.625 | 56927.25 | 52894.5556 | 51546.625 | 61052.3333 | 37561.5 | - | 49923.2951 | (gallons / mo) |  | average
|  | Feed solids | monthly average | (percent) | 3 | 3.375 | 3.2222 | 3.1111 | 3.1111 | 3.75 | 3.2222 | 3.3333 | 3.5 | 3.375 | 3.2222 | 3.75 | 3.75 | 3 | - | 3.331 | (percent) |  | average
|  | Press run time | total | (hours) | 28 | 21.5 | 28.75 | 26.25 | 28.75 | 31.75 | 35.75 | 31 | 27.75 | 30.25 | 31 | 29 | 35.75 | 21.5 | 349.75 | 6.726 | (hours / wk) |  | total; average
|  | Polymer | total added | (pounds) | 192.2 | 148.6 | 198.4 | 195.3 | 195.3 | 223.2 | 266.6 | 226.3 | 201.5 | 257.3 | 257.3 | 210.8 | 266.6 | 148.6 | 2572.8 | 49.4769 | (pounds / wk) |  | total; average
|  | Cake solids | monthly average | (percent) | 31.75 | 32.75 | 29.7778 | 28.8889 | 33.4444 | 31.75 | 32.2222 | 32.2222 | 32.125 | 27.375 | 28.4444 | 32.125 | 33.4444 | 27.375 | - | 31.0729 | (percent) |  | average
|  | Generated | total volume | (cubic yards) | 168 | 144 | 168 | 134 | 215 | 270 | 260 | 216 | 192 | 192 | 182 | 174 | 270 | 134 | 2315 | 44.5192 | (cu. yd. / wk) |  | total; average
|  | Lime | total added | (pounds) | 12555 | 10905 | 6150 | 1560 | 14235 | 19042.5 | 21127.5 | 16260 | 10327.5 |  |  | 12675 | 21127.5 | 1560 | 124837.5 | 2400.7212 | (pounds / wk) |  | total; average
|  | pH | monthly average | (std units) | 12.3712 | 12.3837 | 12.3875 | 12.36 | 12.3756 | 12.3863 | 12.3922 | 12.3733 | 12.3733 |  |  | 12.3914 | 12.3922 | 12.36 | - | 12.3795 | (std units) | 12 | average