## January 08
BRUNSWICK SEWER DISTRICT | [11 empty] | State Discharge License Number W 002600-5L-C-R | [9 empty] | Certifying Official: |  |  | Francis E. McVey | BRUNSWICK SEWER DISTRICT | [13 empty] | State Discharge License Number W 002600-5L-C-R | [11 empty] | BRUNSWICK SEWER DISTRICT | [9 empty] | State Discharge License Number W 002600-5L-C-R
Monthly Report of Treatment Operations : |  |  |  |  | January | 2008 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [12 empty] | General Manager | Monthly Report of Treatment Operations : |  |  |  |  | January | 2008 | [7 empty] | N.P.D.E.S. Permit Number ME 0100102 | [9 empty] | Page 2. |  | Monthly Report of Treatment Operations : |  |  | January | 2008 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [7 empty] | Page 3.
SETTLEABLE
| FLOW | [6 empty] | WEATHER |  |  |  |  | DISINFECTION |  |  | P.H. |  |  | TEMPERATURE |  |  |  | SOLIDS |  |  |  | BIOCHEMICAL OXYGEN DEMAND | [6 empty] | TOTAL SUSPENDED SOLIDS | [6 empty] | SLUDGE DEWATERING | [7 empty] | SLUDGE UTILIZATION |  |  |  | SUMMARY DATA | [11 empty] | HIGH WEEKLY AVERAGE VALUES
|  | Total | Maxim. | Minim. | [8 empty] | Hypo - | [37 empty] | Stored |  |  |  | LOADING |  |  | CONCENTRATION |  |  |  | REPORTING |  |  |  | BOD |  | TSS |  |  | SETTLEABLE SOLIDS
| Totalizer | Flow | Flow | Flow | Flow | Holding | Septic |  | Average | Total | Grit |  | chlorite | Chlorine | [18 empty] | CBOD | [7 empty] | Quantity | Feed | Filter |  | Cake | Sludge | Lime | Average | Quantity |  | or |  |  |  | Monthly | Daily |  | Mo Aver | High Wkly | Daily |  |  |  | Sample
Date | Reading | Treated | (instant.) | (instant.) | By-passed | Received | Added | Conditions | Temp. | Precip. | Removed |  | Used | Residual | E. Coli | Influent | Primary | Effluent | Influent | Primary | Effluent |  | Influent | Primary | Effluent | Date | Influent | Influent | Primary | Primary | Effluent | Effluent | Effluent | Influent | Influent | Primary | Primary | Effluent | Effluent |  | Dewatered | Solids | Operation | Polymer | Dry Solid | Dewatered | Added | pH | Utilized | Site | Spread |  |  |  | Average | Maximum | Units | Minimum | Average | Maximum | Units | Exceptions | Frequency | Type |  | High Weekly Average |  | High Weekly Average |  |  | High Weekly Average
|  | (MG) | (MG) | (MG) | (MG) | (gallons) | (gallons) |  | (deg. F.) | (inches) | (cu. yd.) |  | (gallons) | (mg/L) | (#/100) | (s.u.) | (s.u.) | (s.u.) | (deg. C.) | (deg. C.) | (deg. C.) |  | (ml/L) | (ml/L) | (ml/L) |  | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) |  | (gallons) | (%) | (hours) | (lbs) | (%) | (cu. yd.) | (lbs) | (s.u.) | (cu. yd.) | [16 empty] | (mg / L) | (lbs / day) | (mg / L) | (lbs / day) |  | (mg / L)
6663072
1 | 6665262 | 2.19 | 3.6 | 0.6 | 0.00 | 0 | 0 | CLEAR | 24 | 0.01 | [5 empty] | 6.48 | 6.97 | 6.95 | 11.8 | 11.1 | 10.3 |  | 3 | 0.01 | 0 | 1 | [26 empty] | BOD, 5-day | Reporting : | 350.2764 | 457.1154 | (lbs / day) | 16.7143 | 19.6667 | 22 | (mg / L) | 0 | 03/07 | 24 | Week 1 | 13.3333 | 244.2786 | 15 | 275.4368 |  | 0 | check formulas for designation of weeks
2 | 6667375 | 2.113 | 3.6 | 0.6 | 0.00 | 2350 | 1000 | CLEAR | 19.6 | 0.17 | [5 empty] | 6.82 | 6.85 | 6.87 | 11.5 | 11 | 8.2 |  | 4 | 0.01 | 0 | 2 | 195 | 3436.3719 |  |  | 14 | 246.7139 | 10 | 132 | 2326.1594 |  |  | 14 | 246.7139 | [13 empty] | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24
3 | 6669619 | 2.244 | 3.9 | 0.6 | 0.00 | 3600 | 1750 | CLEAR | 3.9 | 0 |  |  | O | O | O | 7.12 | 7.18 | 7.05 | 11.9 | 10.6 | 9.3 |  | 8 | 0.01 | 0 | 3 | 245 | 4585.1652 |  |  | 12 | 224.5795 | 8 | 208 | 3892.7117 |  |  | 14 | 262.0094 | [25 empty] | Week 2 | 16 | 349.4682 | 21 | 458.8195 |  | 0.0042857 | identifies cell for keyed data entry
4 | 6671859 | 2.24 | 4 | 0.6 | 0.00 | 1000 | 750 | CLEAR | 6.4 | 0.03 | [5 empty] | 7.02 | 7.41 | 6.88 | 12 | 9.4 | 7 |  | 9.5 | 0 | 0 | 4 | 231 | 4315.4496 | 139 | 2596.7424 | 14 | 261.5424 | 10 | 168 | 3138.5088 | 70 | 1307.712 | 17 | 317.5872 |  | 55683 | 2 | 3 | 24.8 | 32 | 12 | 1350 | 12.47 | 12 | EGYPT | STORE
5 | 6674035 | 2.176 | 3.8 | 0.6 | 0.00 | 0 | 0 | CLEAR | 18 | 0.17 |  |  | F | F | F | 7.13 | 8.32 | 7.02 | 12.8 | 10 | 9.7 |  | 10 | 0.01 | 0 | 5 | [38 empty] | Week 3 | 15.6667 | 344.8423 | 23.6667 | 521.0026 |  | 0.0014286
6 | 6676100 | 2.065 | 4 | 0.6 | 0.00 | 200 | 0 | CLEAR | 32.4 | 0.18 | [5 empty] | 6.88 | 7.76 | 7.18 | 12.5 | 10.8 | 10.3 |  | 4.5 | 0.01 | 0 | 6 | [26 empty] | pH | Reporting : | - | - | - | 6.21 | - | 7.18 | (s.u.) | 0 | 01/01 | GR
7 | 6678205 | 2.105 | 3.7 | 0.5 | 0.00 | 3000 | 2000 | CLEAR | 35.2 | 0.02 |  |  | F | F | F | 7.55 | 7.46 | 7.17 | 11.7 | 11 | 10.5 |  | 5.5 | 0.01 | 0 | 7 | [14 empty] | 52176 | 3 | 3.5 | 27.9 | 31 | 24 | 1575 | 12.38 | 24 | EGYPT | STORE |  | Effluent | Permit : | - | - | - | 6 | - | 8.5 | (s.u.) | - | 01/01 | GR | Week 4 | 19.6667 | 423.6998 | 21.6667 | 467.1929 |  | 0.0028571
8 | 6680347 | 2.142 | 4.5 | 0.6 | 0.00 | 1000 | 3000 | CLEAR | 43.1 | 0 | [5 empty] | 7.45 | 7.68 | 6.99 | 12.2 | 11.8 | 12.3 |  | 10 | 0.01 | 0.01 | 8
9 | 6682857 | 2.51 | 5.2 | 0.8 | 0.00 | 150 | 1000 | RAIN | 45.6 | 0.04 | [5 empty] | 7.24 | 7.4 | 6.83 | 12.2 | 11.6 | 12.1 |  | 9 | 0.01 | 0.01 | 9 | 211 | 4416.9474 |  |  | 17 | 355.8678 | 13 | 178 | 3726.1452 |  |  | 22 | 460.5348 | [25 empty] | Week 5
10 | 6685534 | 2.677 | 4.7 | 0.8 | 0.00 | 5000 | 3000 | CLEAR | 40.1 | 0 | [5 empty] | 7.25 | 7.33 | 6.69 | 11.8 | 11.7 | 11.4 |  | 7.5 | 0.01 | 0 | 10 | 211 | 4710.824 |  |  | 14 | 312.5665 | 10 | 254 | 5670.8497 |  |  | 19 | 424.1974 |  | 50062 | 3 | 3.25 | 24.8 | 33 | 24 | 1560 | 12.41 | 24 | EGYPT | STORE
11 | 6688214 | 2.68 | 4.6 | 1.2 | 0.00 | 2000 | 1000 | RAIN | 33.9 | 0.8 |  |  | F | F | F | 7.16 | 7.47 | 6.89 | 11.5 | 11.1 | 11.4 |  | 6 | 0.01 | 0.01 | 11 | 135 | 3017.412 | 146 | 3263.2752 | 17 | 379.9704 | 13 | 116 | 2592.7392 | 73 | 1631.6376 | 22 | 491.7264 | [13 empty] | TSS | Reporting : | 446.4211 | 649.1522 | (lbs / day) | 21.2143 | 23.6667 | 29 | (mg / L) | 0 | 03/07 | 24
12 | 6691337 | 3.123 | 4.4 | 1 | 0.00 | 0 | 0 | CLOUDY | 35.2 | 0.01 | [5 empty] | 6.99 | 7.37 | 6.9 | 10.4 | 10.2 | 10.4 |  | 3.5 | 0.1 | 0 | 12 | [26 empty] | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24 | Maximum | 19.6667 | 423.6998 | 23.6667 | 521.0026 |  | 0.0042857
13 | 6694238 | 2.901 | 4.4 | 1 | 0.00 | 1000 | 1000 | CLEAR | 29.4 | 0 |  |  | O | O | O | 6.73 | 7.6 | 7.18 | 10.5 | 10.1 | 10.2 |  | 1.5 | 0 | 0 | 13
14 | 6696970 | 2.732 | 4.2 | 0.9 | 0.00 | 0 | 0 | SNOW | 24.3 | 0 | [5 empty] | 6.91 | 7.41 | 7.14 | 11.6 | 10.1 | 9.1 |  | 6 | 0.01 | 0 | 14
15 | 6699716 | 2.746 | 4.1 | 0.9 | 0.00 | 1000 | 2000 | CLEAR | 22.1 | 0.15 |  |  | R | R | R | 6.9 | 7.45 | 7.09 | 10.9 | 9.8 | 8.7 |  | 5 | 0.2 | 0 | 15 | [14 empty] | 70375 | 3 | 4.5 | 34.1 | 32 | 24 | 2025 | 12.43 | 24 | EGYPT | STORE
16 | 6702366 | 2.65 | 4.2 | 0.9 | 0.00 | 2000 | 2000 | CLEAR | 21.3 | 0 | [5 empty] | 6.94 | 7.45 | 6.93 | 11.4 | 9.9 | 9.4 |  | 6.5 | 0.01 | 0.01 | 16 | 205 | 4530.705 |  |  | 17 | 375.717 | 14 | 218 | 4818.018 |  |  | 19 | 419.919 | [13 empty] | SETTLEABLE
17 | 6705050 | 2.684 | 4.6 | 0.8 | 0.00 | 1000 | 1000 | CLEAR | 19 | 0.01 | [5 empty] | 7.12 | 7.4 | 6.79 | 11.1 | 9.6 | 8.6 |  | 6 | 0.01 | 0 | 17 | 209 | 4678.373 |  |  | 16 | 358.153 | 11 | 170 | 3805.3752 |  |  | 29 | 649.1522 |  | 35344 | 4 | 2.75 | 18.6 | 34 | 20 | 1237.5 | 12.34 | 20 | EGYPT | STORE |  | SOLIDS | Reporting : | - | - | - | - | 0.0042857 | 0.01 | (mg / L) | 0 | 01/01 | GR
18 | 6707625 | 2.575 | 5.5 | 1 | 0.00 | 750 | 1000 | RAIN | 35.5 | 0.66 | [5 empty] | 7.22 | 7.24 | 6.76 | 11.1 | 9.8 | 9.8 |  | 18 | 0.1 | 0 | 18 | 211 | 4531.3305 | 147 | 3156.8985 | 14 | 300.657 | 19 | 154 | 3307.227 | 64 | 1374.432 | 23 | 493.9365 | [13 empty] | Effluent | Permit : | - | - | - | - | (Report) | 0.3 | (mg / L) | - | 01/01 | GR
19 | 6710647 | 3.022 | 4.3 | 1 | 0.00 | 0 | 0 | CLEAR | 27.8 | 0 |  |  | S | S | S | 6.27 | 6.71 | 6.65 | 11.4 | 10.6 | 8.9 |  | 2.5 | 0.01 | 0 | 19
20 | 6713361 | 2.714 | 4.2 | 1 | 0.00 | 1000 | 0 | CLOUDY | 20.3 | 0 | [5 empty] | 6.81 | 7.04 | 6.66 | 10.9 | 8.3 | 8.2 |  | 4.5 | 0.01 | 0 | 20
21 | 6716005 | 2.644 | 4.2 | 0.8 | 0.00 | 0 | 0 | CLOUDY | 13.4 | 0 |  |  | E | E | E | 7.04 | 7.12 | 6.8 | 10.7 | 9.1 | 7.1 |  | 4.5 | 0.1 | 0.01 | 21
22 | 6718670 | 2.665 | 4.4 | 0.8 | 0.00 | 2750 | 0 | CLEAR | 23.1 | 0 | [5 empty] | 6.78 | 6.87 | 6.21 | 10.7 | 11 | 9.1 |  | 5 | 0.01 | 0.01 | 22 | [14 empty] | 71330 | 3 | 4.75 | 37.2 | 31 | 24 | 2137.5 | 12.38 | 24 | EGYPT | STORE |  | FLOW | Reporting : | 2.5172 | 3.123 | (MGD) | - | - | - | - | 0 | 99/99 | RC |  |  |  | CBOD
23 | 6721280 | 2.61 | 4.2 | 0.8 | 0.00 | 1350 | 2000 | CLEAR | 29.6 | 0 |  |  | A | A | A | 6.91 | 6.99 | 6.7 | 11.4 | 11.5 | 10.2 |  | 12 | 0.01 | 0 | 23 | 218 | 4745.2932 |  |  | 21 | 457.1154 | 15 | 158 | 3439.2492 |  |  | 25 | 544.185 | [13 empty] | Effluent | Permit : | 3.85 | (Report) | (MGD) | - | - | - | - | - | 99/99 | RC
24 | 6723830 | 2.55 | 4.6 | 0.8 | 0.00 | 3200 | 0 | CLOUDY | 20.9 | 0 | [5 empty] | 7.12 | 7.23 | 6.91 | 11.3 | 11.1 | 10.6 |  | 5 | 0.01 | 0 | 24 | 216 | 4593.672 |  |  | 18 | 382.806 | 13 | 142 | 3019.914 |  |  | 17 | 361.539 |  | 31877 | 3 | 2.5 | 15.5 | 32 | 12 | 1200 | 12.36 | 12 | EGYPT | STORE | [16 empty] | % Removal
25 | 6726415 | 2.585 | 4 | 0.7 | 0.00 | 1800 | 1000 | CLEAR | 16.5 | 0 |  |  | S | S | S | 6.97 | 7.02 | 6.46 | 10.8 | 10.5 | 8.8 |  | 4.5 | 0.1 | 0 | 25 | 219 | 4721.3991 | 155 | 3341.6295 | 20 | 431.178 | 14 | 202 | 4354.8978 | 64 | 1379.7696 | 23 | 495.8547
26 | 6728891 | 2.476 | 4.2 | 0.8 | 0.00 | 0 | 0 | CLEAR | 21.9 | 0 | [5 empty] | 6.85 | 7.08 | 6.49 | 10.7 | 9.4 | 8.9 |  | 4 | 0.01 | 0 | 26 | [41 empty] | 93.9273
27 | 6731317 | 2.426 | 4.2 | 0.6 | 0.00 | 0 | 0 | SNOW | 22.1 | 0 |  |  | O | O | O | 6.93 | 7.1 | 6.31 | 10.6 | 9.2 | 9 |  | 6 | 0.01 | 0 | 27 | [26 empty] | BOD, 5-day | Reporting : | - | - | - | 92.0364 | - | - | (percent) | 0 | 01/30 | CA
28 | 6733710 | 2.393 | 4.4 | 0.7 | 0.00 | 6700 | 3500 | CLOUDY | 25.4 | 0 | [5 empty] | 6.89 | 7.19 | 6.68 | 10.5 | 9.8 | 8.7 |  | 4.5 | 0.01 | 0.01 | 28 | [14 empty] | 67746 | 3 | 4 | 31 | 32 | 24 | 1800 | 12.41 | 24 | EGYPT | STORE |  | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
29 | 6736205 | 2.495 | 4.4 | 0.6 | 0.00 | 3500 | 1000 | CLEAR | 32.7 | 0 |  |  | N | N | N | 7.06 | 7.1 | 6.78 | 10.9 | 10.2 | 8.8 |  | 5 | 0.01 | 0 | 29
30 | 6738650 | 2.445 | 4.8 | 0.7 | 0.00 | 0 | 3750 | RAIN | 38.9 | 0.15 | [5 empty] | 6.86 | 6.94 | 6.34 | 10.7 | 10.9 | 11.2 |  | 5.5 | 0.01 | 0 | 30 | 226 | 4608.4338 |  |  | 22 | 448.6086 | 16 | 232 | 4730.7816 |  |  | 29 | 591.3477
31 | 6741104 | 2.454 | 4 | 0.7 | 0.00 | 1200 | 1000 | CLEAR | 27.1 | 0 | [5 empty] | 6.99 | 7.3 | 6.59 | 11.1 | 10.2 | 9.7 |  | 5 | 0.1 | 0 | 31 | 229 | 4686.7964 |  |  | 18 | 368.3945 | 12 | 240 | 4911.9264 |  |  | 24 | 491.1926 |  | 48226 | 4 | 3 | 21.7 | 33 | 21 | 1530 | 12.45 | 21 | EGYPT | STORE
[53 empty] | TSS | Reporting : | - | - | - | 88.4526 | - | - | (percent) | 0 | 01/30 | CA
Total | 78032 | 78.032 | - | - | 0 | 45550 | 32750 | - | - | 2.4 | 0.0 |  | 0 | - | - | - | - | - | - | - | - |  | - | - | - | Total | - | - | - | - | - | - | - | - | - | - | - | - | - |  | 482819 | - | 31.25 | 235.6 | - | 185 | 14415 | - | 185 | - | - |  | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
Maximum | - | 3.123 | 5.5 | 1.2 | 0 | 6700 | 3750 | - | 45.6 | 0.8 | - |  | - | - | - | 7.55 | 8.32 | 7.18 | 12.8 | 11.8 | 12.3 |  | 18 | 0.2 | 0.01 | Maximum | 245 | 4745.2932 | 155 | 3341.6295 | 22 | 457.1154 | 19 | 254 | 5670.8497 | 73 | 1631.6376 | 29 | 649.1522 |  | - | 4 | - | - | 34 | - | - | 12.47 | - | - | -
Minimum | - | 2.065 | 3.6 | 0.5 | 0 | 0 | 0 | - | 3.9 | 0 | - |  | - | - | - | 6.27 | 6.71 | 6.21 | 10.4 | 8.3 | 7 |  | 1.5 | 0 | 0 | Minimum | 135 | 3017.412 | 139 | 2596.7424 | 12 | 224.5795 | 8 | 116 | 2326.1594 | 64 | 1307.712 | 14 | 246.7139 |  | - | 2 | - | - | 31 | - | - | 12.34 | - | - | -
Average | - | 2.5172 | 4.2871 | 0.77419 | 0.000 | 1469.3548 | 1056.4516 | - | 26.0871 | 0.077419 | - |  | - | - | - | 6.9803 | 7.2723 | 6.8029 | 11.3097 | 10.3677 | 9.6097 |  | 6.1774 | 0.03 | 0.0022581 | Average | 211.5 | 4398.4409 | 146.75 | 3089.6364 | 16.7143 | 350.2764 | 12.7143 | 183.7143 | 3838.1788 | 67.75 | 1423.3878 | 21.2143 | 446.4211 |  | 53646.5556 | 3.1111 | 3.4722 | 26.1778 | 32.2222 | 20.5556 | 1601.6667 | 12.4033 | 20.5556 | - | -
[13 empty] | Geometric Mean : |  | - | [14 empty] | Percent Removal : |  | 92.0364 |  |  |  | Percent Removal : |  | 88.4526

## Graph Jan08
Plant Capacity
3.85 mgd

## February 08
BRUNSWICK SEWER DISTRICT | [11 empty] | State Discharge License Number W 002600-5L-C-R | [9 empty] | Certifying Official: |  |  | Francis E. McVey | BRUNSWICK SEWER DISTRICT | [13 empty] | State Discharge License Number W 002600-5L-C-R | [11 empty] | BRUNSWICK SEWER DISTRICT | [9 empty] | State Discharge License Number W 002600-5L-C-R
Monthly Report of Treatment Operations : |  |  |  |  | February | 2008 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [12 empty] | General Manager | Monthly Report of Treatment Operations : |  |  |  |  | February | 2008 | [7 empty] | N.P.D.E.S. Permit Number ME 0100102 | [9 empty] | Page 2. |  | Monthly Report of Treatment Operations : |  |  | February | 2008 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [7 empty] | Page 3.
SETTLEABLE
| FLOW | [6 empty] | WEATHER |  |  |  |  | DISINFECTION |  |  | P.H. |  |  | TEMPERATURE |  |  |  | SOLIDS |  |  |  | BIOCHEMICAL OXYGEN DEMAND | [6 empty] | TOTAL SUSPENDED SOLIDS | [6 empty] | SLUDGE DEWATERING | [7 empty] | SLUDGE UTILIZATION |  |  |  | SUMMARY DATA | [11 empty] | HIGH WEEKLY AVERAGE VALUES
|  | Total | Maxim. | Minim. | [8 empty] | Hypo - | [37 empty] | Stored |  |  |  | LOADING |  |  | CONCENTRATION |  |  |  | REPORTING |  |  |  | BOD |  | TSS |  |  | SETTLEABLE SOLIDS
| Totalizer | Flow | Flow | Flow | Flow | Holding | Septic |  | Average | Total | Grit |  | chlorite | Chlorine | [18 empty] | CBOD | [7 empty] | Quantity | Feed | Filter |  | Cake | Sludge | Lime | Average | Quantity |  | or |  |  |  | Monthly | Daily |  | Mo Aver | High Wkly | Daily |  |  |  | Sample
Date | Reading | Treated | (instant.) | (instant.) | By-passed | Received | Added | Conditions | Temp. | Precip. | Removed |  | Used | Residual | E. Coli | Influent | Primary | Effluent | Influent | Primary | Effluent |  | Influent | Primary | Effluent | Date | Influent | Influent | Primary | Primary | Effluent | Effluent | Effluent | Influent | Influent | Primary | Primary | Effluent | Effluent |  | Dewatered | Solids | Operation | Polymer | Dry Solid | Dewatered | Added | pH | Utilized | Site | Spread |  |  |  | Average | Maximum | Units | Minimum | Average | Maximum | Units | Exceptions | Frequency | Type |  | High Weekly Average |  | High Weekly Average |  |  | High Weekly Average
|  | (MG) | (MG) | (MG) | (MG) | (gallons) | (gallons) |  | (deg. F.) | (inches) | (cu. yd.) |  | (gallons) | (mg/L) | (#/100) | (s.u.) | (s.u.) | (s.u.) | (deg. C.) | (deg. C.) | (deg. C.) |  | (ml/L) | (ml/L) | (ml/L) |  | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) |  | (gallons) | (%) | (hours) | (lbs) | (%) | (cu. yd.) | (lbs) | (s.u.) | (cu. yd.) | [16 empty] | (mg / L) | (lbs / day) | (mg / L) | (lbs / day) |  | (mg / L)
6741104
1 | 6743450 | 2.346 | 5.4 | 1 | 0.00 | 0 | 1000 | CLEAR | 26 | 0.55 | [5 empty] | 7.11 | 7.16 | 6.47 | 11.7 | 11.1 | 10.5 |  | 8.5 | 0.01 | 0 | 1 | 246 | 4813.1474 | 176 | 3443.5526 | 20 | 391.3128 | 15 | 206 | 4030.5218 | 86 | 1682.645 | 28 | 547.8379 | [13 empty] | BOD, 5-day | Reporting : | 415.2326 | 624.3991 | (lbs / day) | 15.4615 | 20 | 20 | (mg / L) | 0 | 03/07 | 24 | Week 1 | 20 | 403 | 27 | 543 |  | 0 | check formulas for designation of weeks
2 | 6746445 | 2.995 | 4.8 | 1 | 0.00 | 0 | 0 | CLEAR | 36.7 | 0.78 | [5 empty] | 6.54 | 6.89 | 6.21 | 10.3 | 9.1 | 10.4 |  | 2 | 0.01 | 0 | 2 | [26 empty] | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24
3 | 6749447 | 3.002 | 4.4 | 1 | 0.00 | 0 | 0 | CLOUDY | 32.4 | 0 |  |  | O | O | O | 6.63 | 6.85 | 6.75 | 10.1 | 10 | 10.1 |  | 1 | 0.01 | 0 | 3 | [38 empty] | Week 2 | 16 | 379.5923 | 22 | 522.0673 |  | 0.0014286 | identifies cell for keyed data entry
4 | 6752217 | 2.77 | 4.3 | 1 | 0.00 | 2000 | 4750 | CLOUDY | 32.1 | 0 | [5 empty] | 6.42 | 6.91 | 6.8 | 11.2 | 9.9 | 10 |  | 5.5 | 0.01 | 0 | 4
5 | 6755022 | 2.805 | 4.2 | 1 | 0.00 | 0 | 1000 | SNOW | 33.3 | 0.33 |  |  | F | F | F | 6.99 | 5.59 | 6.09 | 11.3 | 10.4 | 9.9 |  | 9 | 2.5 | 0.01 | 5 | [14 empty] | 65517 | 4 | 3.75 | 31 | 32 | 24 | 1800 | 12.32 | 24 | EGYPT | STORE | [13 empty] | Week 3 | 15.6667 | 428.8039 | 19.3333 | 535.5281 |  | 0
6 | 6757783 | 2.761 | 4.4 | 1.1 | 0.00 | 1200 | 1000 | CLOUDY | 33.4 | 0.4 | [5 empty] | 6.9 | 6.88 | 6.61 | 12 | 12.9 | 11.9 |  | 4 | 0.01 | 0 | 6 | 208 | 4789.5619 |  |  | 17 | 391.4546 | 13 | 208 | 4789.5619 |  |  | 24 | 552.6418 | [13 empty] | pH | Reporting : | - | - | - | 6.09 | - | 7.01 | (s.u.) | 0 | 01/01 | GR
7 | 6760720 | 2.937 | 4.4 | 1 | 0.00 | 1500 | 1000 | LT SNOW | 23.4 | 0 |  |  | F | F | F | 6.74 | 6.79 | 6.84 | 10.2 | 10.8 | 9.8 |  | 3 | 0.01 | 0 | 7 | 174 | 4262.0569 |  |  | 16 | 391.9133 | 12 | 176 | 4311.0461 |  |  | 23 | 563.3753 | [13 empty] | Effluent | Permit : | - | - | - | 6 | - | 8.5 | (s.u.) | - | 01/01 | GR | Week 4 | 15.3333 | 519.0899 | 20 | 676.3406 |  | 0.0014286
8 | 6763561 | 2.841 | 4.4 | 1 | 0.00 | 300 | 1000 | LT SNOW | 21.1 | 0 | [5 empty] | 6.97 | 7.06 | 6.7 | 10.6 | 9.2 | 8.3 |  | 5 | 0.01 | 0 | 8 | 168 | 3980.5819 | 129 | 3056.5183 | 15 | 355.4091 | 10 | 166 | 3933.194 | 66 | 1563.8 | 19 | 450.1849 |  | 60667 | 3 | 3.75 | 24.8 | 32 | 24 | 1575 | 12.38 | 24 | EGYPT | STORE
9 | 6766259 | 2.698 | 4.2 | 1 | 0.00 | 0 | 0 | CLEAR | 22.4 | 0.2 | [5 empty] | 6.31 | 6.54 | 6.56 | 10.7 | 9.8 | 9.4 |  | 2.5 | 0.01 | 0 | 9 | [38 empty] | Week 5 | 13.3333 | 341.4174 | 18.6667 | 478.5714
10 | 6768877 | 2.618 | 4.3 | 0.9 | 0.00 | 0 | 0 | SNOW | 32.9 | 0.5 | [5 empty] | 6.3 | 6.59 | 6.64 | 10.4 | 10 | 10.1 |  | 2 | 0.01 | 0 | 10
11 | 6771441 | 2.564 | 4.3 | 1 | 0.00 | 1000 | 1000 | CLOUDY | 15.5 | 0 |  |  | F | F | F | 6.9 | 6.95 | 6.82 | 11.1 | 9.8 | 8.6 |  | 5.5 | 0.01 | 0 | 11 | [26 empty] | TSS | Reporting : | 552.72 | 808.0459 | (lbs / day) | 20.6154 | 27 | 28 | (mg / L) | 0 | 03/07 | 24
12 | 6774115 | 2.674 | 4.2 | 1 | 0.00 | 4500 | 1000 | CLOUDY | 18.3 | 0.03 | [5 empty] | 6.59 | 6.95 | 6.63 | 11.1 | 9.8 | 8.7 |  | 8.5 | 0.3 | 0 | 12 | [14 empty] | 68041 | 4 | 4.25 | 34.1 | 31 | 24 | 1785 | 12.36 | 24 | EGYPT | STORE |  | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24 | Maximum | 20 | 519.0899 | 27 | 676.3406 |  | 0.0014286
13 | 6776718 | 2.603 | 7.7 | 1.2 | 0.00 | 0 | 0 | SNOW | 28.3 | 1.19 |  |  | O | O | O | 7 | 7.16 | 6.7 | 10.9 | 9.5 | 8.9 |  | 10 | 0.01 | 0 | 13 | 178 | 3864.2056 |  |  | 17 | 369.0533 | 11 | 176 | 3820.7875 |  |  | 19 | 412.4714
14 | 6780570 | 3.852 | 5 | 1.4 | 0.00 | 2500 | 500 | CLEAR | 30.2 | 0.34 | [5 empty] | 6.53 | 6.95 | 7.01 | 10.4 | 9.3 | 7.5 |  | 5.5 | 0.01 | 0 | 14 | 152 | 4883.1034 |  |  | 15 | 481.8852 | 11 | 164 | 5268.6115 |  |  | 20 | 642.5136
15 | 6784051 | 3.481 | 5.3 | 1.4 | 0.00 | 0 | 1000 | CLEAR | 31.1 | 0.21 |  |  | R | R | R | 6.6 | 6.72 | 6.76 | 10.4 | 9.4 | 8.8 |  | 7.5 | 0.01 | 0 | 15 | 143 | 4151.5102 | 105 | 3048.3117 | 15 | 435.4731 | 11 | 96 | 2787.0278 | 44 | 1277.3878 | 19 | 551.5993
16 | 6787301 | 3.25 | 4.8 | 1.2 | 0.00 | 0 | 0 | CLEAR | 17.7 | 0 | [5 empty] | 6.37 | 6.74 | 6.64 | 10 | 9.2 | 9.1 |  | 2.5 | 0.01 | 0 | 16 | [26 empty] | SETTLEABLE
17 | 6790383 | 3.082 | 5 | 1.6 | 0.00 | 0 | 0 | CLEAR | 22.4 | 0.17 | [5 empty] | 6.67 | 6.75 | 6.91 | 10.3 | 9.2 | 8.6 |  | 2 | 0 | 0 | 17 | [26 empty] | SOLIDS | Reporting : | - | - | - | - | 0.0014286 | 0.01 | (mg / L) | 0 | 01/01 | GR
18 | 6793703 | 3.32 | 8.2 | 2.5 | 0.00 | 0 | 0 | RAIN | 43.2 | 1.09 | [5 empty] | 6.54 | 6.64 | 6.7 | 9.2 | 8.6 | 10.1 |  | 2.5 | 0.01 | 0 | 18 | [26 empty] | Effluent | Permit : | - | - | - | - | (Report) | 0.3 | (mg / L) | - | 01/01 | GR
19 | 6798956 | 5.253 | 6 | 2 | 0.00 | 1000 | 5000 | CLEAR | 35.8 | 0.01 |  |  | S | S | S | 6.06 | 6.27 | 6.37 | 11 | 9.7 | 9.2 |  | 2 | 0.4 | 0.01 | 19 | [14 empty] | 76749 | 4 | 4.5 | 37.2 | 32 | 24 | 2025 | 12.39 | 24 | EGYPT | STORE
20 | 6803360 | 4.404 | 5.4 | 1.9 | 0.00 | 2200 | 1000 | CLEAR | 25.2 | 0.01 | [5 empty] | 6.62 | 6.91 | 6.97 | 10.3 | 10.1 | 9 |  | 5 | 0.1 | 0 | 20 | 112 | 4113.6883 |  |  | 17 | 624.3991 | 14 | 102 | 3746.3947 |  |  | 22 | 808.0459
21 | 6807307 | 3.947 | 5.4 | 1.8 | 0.00 | 0 | 0 | CLEAR | 17.8 | 0 |  |  | E | E | E | 6.79 | 6.82 | 6.95 | 10 | 9.5 | 7.5 |  | 6 | 0.2 | 0 | 21 | 129 | 4246.4194 |  |  | 13 | 427.9337 | 12 | 118 | 3884.3216 |  |  | 16 | 526.6877 |  | 25186 | 5 | 3 | 12.4 | 32 | 12 | 990 | 12.37 | 12 | EGYPT | STORE
22 | 6811091 | 3.784 | 5.4 | 1.6 | 0.00 | 0 | 0 | CLEAR | 17.3 | 0 | [5 empty] | 6.58 | 6.69 | 6.75 | 9.9 | 8.7 | 8.3 |  | 4 | 0.01 | 0 | 22 | 205 | 6469.5048 | 126 | 3976.3786 | 16 | 504.937 | 14 | 224 | 7069.1174 | 77 | 2430.0091 | 22 | 694.2883 | [13 empty] | FLOW | Reporting : | 3.1893 | 5.253 | (MGD) | - | - | - | - | 0 | 99/99 | RC |  |  |  | CBOD
23 | 6814653 | 3.562 | 4.8 | 1.3 | 0.00 | 0 | 0 | CLOUDY | 24.9 | 0.13 |  |  | A | A | A | 6.56 | 6.91 | 6.95 | 10 | 8.3 | 7.7 |  | 3 | 0.01 | 0 | 23 | [26 empty] | Effluent | Permit : | 3.85 | (Report) | (MGD) | - | - | - | - | - | 99/99 | RC
24 | 6817961 | 3.308 | 4.8 | 1.4 | 0.00 | 0 | 0 | CLEAR | 26.5 | 0 | [5 empty] | 6.5 | 6.78 | 6.8 | 10.1 | 8.6 | 8.8 |  | 1.5 | 0.01 | 0 | 24 | [41 empty] | % Removal
25 | 6821207 | 3.246 | 4.6 | 1.6 | 0.00 | 1000 | 1500 | CLEAR | 26.6 | 0 |  |  | S | S | S | 6.63 | 6.9 | 6.93 | 10.5 | 8.9 | 9.2 |  | 7 | 0.1 | 0 | 25 | [14 empty] | 41885 | 3 | 5 | 18.6 | 33 | 12 | 1950 | 12.37 | 12 | EGYPT | STORE
26 | 6824382 | 3.175 | 5 | 1.4 | 0.00 | 4800 | 0 | CLOUDY | 28.8 | 0.01 | [5 empty] | 6.58 | 6.87 | 6.89 | 10.1 | 9.9 | 9.8 |  | 6.5 | 0.7 | 0 | 26 | [14 empty] | 23919 | 4 | 3.75 | 9.3 | 32 | 12 | 1575 | 12.31 | 12 | EGYPT | STORE | [16 empty] | 93.0378
27 | 6827477 | 3.095 | 4.9 | 1.4 | 0.00 | 0 | 0 | CLOUDY | 32.8 | 0.45 |  |  | O | O | O | 6.54 | 6.64 | 6.62 | 9.8 | 9.3 | 9.1 |  | 4 | 0.01 | 0 | 27 | 147 | 3794.4081 |  |  | 14 | 361.3722 | 10 | 130 | 3355.599 |  |  | 22 | 567.8706 | [13 empty] | BOD, 5-day | Reporting : | - | - | - | 90.6498 | - | - | (percent) | 0 | 01/30 | CA
28 | 6830562 | 3.085 | 4.6 | 1.2 | 0.00 | 1300 | 2000 | CLOUDY | 21.6 | 0.11 | [5 empty] | 6.6 | 6.78 | 6.71 | 10.3 | 9.3 | 8.2 |  | 5.5 | 0.01 | 0.01 | 28 | 153 | 3936.5217 |  |  | 12 | 308.7468 | 8 | 222 | 5711.8158 |  |  | 18 | 463.1202 |  | 40734 | 4 | 2.75 | 21.7 | 34 | 20 | 1402.5 | 12.42 | 20 | EGYPT | STORE |  | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
29 | 6833595 | 3.033 | 4.4 | 1.1 | 0.00 | 4900 | 1000 | CLEAR | 13 | 0.04 |  |  | N | N | N | 6.93 | 7.1 | 6.97 | 9.9 | 8.8 | 8.2 |  | 7 | 0.01 | 0 | 29 | 175 | 4426.6635 | 129 | 3263.0834 | 14 | 354.1331 | 10 | 158 | 3996.6448 | 55 | 1391.2371 | 16 | 404.7235
30 | [25 empty] | 30
31 | [25 empty] | 31
[53 empty] | TSS | Reporting : | - | - | - | 87.5116 | - | - | (percent) | 0 | 01/30 | CA
Total | 92491 | 92.491 | - | - | 0 | 28200 | 23750 | - | - | 6.55 | 0.0 |  | 0 | - | - | - | - | - | - | - | - |  | - | - | - | Total | - | - | - | - | - | - | - | - | - | - | - | - | - |  | 402698 | - | 30.75 | 189.1 | - | 152 | 13102.5 | - | 152 | - | - |  | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
Maximum | - | 5.253 | 8.2 | 2.5 | 0 | 4900 | 5000 | - | 43.2 | 1.19 | - |  | - | - | - | 7.11 | 7.16 | 7.01 | 12 | 12.9 | 11.9 |  | 10 | 2.5 | 0.01 | Maximum | 246 | 6469.5048 | 176 | 3976.3786 | 20 | 624.3991 | 15 | 224 | 7069.1174 | 86 | 2430.0091 | 28 | 808.0459 |  | - | 5 | - | - | 34 | - | - | 12.42 | - | - | -
Minimum | - | 2.346 | 4.2 | 0.9 | 0 | 0 | 0 | - | 13 | 0 | - |  | - | - | - | 6.06 | 5.59 | 6.09 | 9.2 | 8.3 | 7.5 |  | 1 | 0 | 0 | Minimum | 112 | 3794.4081 | 105 | 3048.3117 | 12 | 308.7468 | 8 | 96 | 2787.0278 | 44 | 1277.3878 | 16 | 404.7235 |  | - | 3 | - | - | 31 | - | - | 12.31 | - | - | -
Average | - | 3.1893 | 4.9862 | 1.3103 | 0.000 | 972.4138 | 818.9655 | - | 26.5759 | 0.22586 | - |  | - | - | - | 6.6379 | 6.7859 | 6.7155 | 10.4759 | 9.6241 | 9.1621 |  | 4.7586 | 0.15552 | 0.0010345 | Average | 168.4615 | 4440.8749 | 133 | 3357.5689 | 15.4615 | 415.2326 | 11.6154 | 165.0769 | 4361.8957 | 65.6 | 1669.0158 | 20.6154 | 552.72 |  | 50337.25 | 3.875 | 3.8438 | 23.6375 | 32.25 | 19 | 1637.8125 | 12.365 | 19 | - | -
[13 empty] | Geometric Mean : |  | - | [14 empty] | Percent Removal : |  | 90.6498 |  |  |  | Percent Removal : |  | 87.5116

## Graph Feb08
Plant Capacity
3.85 mgd

## March 08
BRUNSWICK SEWER DISTRICT | [11 empty] | State Discharge License Number W 002600-5L-C-R | [9 empty] | Certifying Official: |  |  | Francis E. McVey | BRUNSWICK SEWER DISTRICT | [14 empty] | State Discharge License Number W 002600-5L-C-R | [11 empty] | BRUNSWICK SEWER DISTRICT | [9 empty] | State Discharge License Number W 002600-5L-C-R
Monthly Report of Treatment Operations : |  |  |  |  | March | 2008 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [12 empty] | General Manager | Monthly Report of Treatment Operations : | [5 empty] | March | 2008 | [7 empty] | N.P.D.E.S. Permit Number ME 0100102 | [9 empty] | Page 2. |  | Monthly Report of Treatment Operations : |  |  | March | 2008 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [7 empty] | Page 3.
SETTLEABLE
| FLOW | [6 empty] | WEATHER |  |  |  |  | DISINFECTION |  |  | P.H. |  |  | TEMPERATURE |  |  |  | SOLIDS |  |  |  |  | BIOCHEMICAL OXYGEN DEMAND | [6 empty] | TOTAL SUSPENDED SOLIDS | [6 empty] | SLUDGE DEWATERING | [7 empty] | SLUDGE UTILIZATION |  |  |  | SUMMARY DATA | [11 empty] | HIGH WEEKLY AVERAGE VALUES
|  | Total | Maxim. | Minim. | [8 empty] | Hypo - | [38 empty] | Stored |  |  |  | LOADING |  |  | CONCENTRATION |  |  |  | REPORTING |  |  |  | BOD |  | TSS |  |  | SETTLEABLE SOLIDS
| Totalizer | Flow | Flow | Flow | Flow | Holding | Septic |  | Average | Total | Grit |  | chlorite | Chlorine | [19 empty] | CBOD | [7 empty] | Quantity | Feed | Filter |  | Cake | Sludge | Lime | Average | Quantity |  | or |  |  |  | Monthly | Daily |  | Mo Aver | High Wkly | Daily |  |  |  | Sample
Date | Reading | Treated | (instant.) | (instant.) | By-passed | Received | Added | Conditions | Temp. | Precip. | Removed |  | Used | Residual | E. Coli | Influent | Primary | Effluent | Influent | Primary | Effluent |  | Influent | Primary | Effluent | Date |  | Influent | Influent | Primary | Primary | Effluent | Effluent | Effluent | Influent | Influent | Primary | Primary | Effluent | Effluent |  | Dewatered | Solids | Operation | Polymer | Dry Solid | Dewatered | Added | pH | Utilized | Site | Spread |  |  |  | Average | Maximum | Units | Minimum | Average | Maximum | Units | Exceptions | Frequency | Type |  | High Weekly Average |  | High Weekly Average |  |  | High Weekly Average
|  | (MG) | (MG) | (MG) | (MG) | (gallons) | (gallons) |  | (deg. F.) | (inches) | (cu. yd.) |  | (gallons) | (mg/L) | (#/100) | (s.u.) | (s.u.) | (s.u.) | (deg. C.) | (deg. C.) | (deg. C.) |  | (ml/L) | (ml/L) | (ml/L) |  |  | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) |  | (gallons) | (%) | (hours) | (lbs) | (%) | (cu. yd.) | (lbs) | (s.u.) | (cu. yd.) | [16 empty] | (mg / L) | (lbs / day) | (mg / L) | (lbs / day) |  | (mg / L)
6833595
1 | 6836578 | 2.983 | 4.4 | 1.1 | 0.00 | 0 | 0 | SNOW | 29.9 | 0.33 | [5 empty] | 6.38 | 6.51 | 6.52 | 9.7 | 8.6 | 8.6 |  | 2.5 | 0 | 0 | 1 | [27 empty] | BOD, 5-day | Reporting : | 454.302 | 676.2906 | (lbs / day) | 13.9167 | 16.6667 | 18 | (mg / L) | 0 | 03/07 | 24 | Week 1 | 16.6667 | 488.2125 | 19.3333 | 565.9635 |  | 0 | check formulas for designation of weeks
2 | 6839416 | 2.838 | 4.6 | 1 | 0.00 | 0 | 0 | CLEAR | 29.7 | 0.06 | [5 empty] | 6.59 | 6.93 | 6.77 | 9.7 | 8.6 | 8.7 |  | 4 | 0.01 | 0 | 2 | [27 empty] | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24
3 | 6842266 | 2.85 | 4.8 | 1.1 | 0.00 | 0 | 2000 | CLEAR | 25.1 | 0.11 |  |  | O | O | O | 6.6 | 7.4 | 7.07 | 10.6 | 9.1 | 9 |  | 5 | 0.3 | 0.01 | 3 | [15 empty] | 51817 | 4 | 3.25 | 27.9 | 33 | 24 | 1560 | 12.4 | 24 | EGYPT | STORE | [13 empty] | Week 2 | 14 | 456.9903 | 18.3333 | 597.4303 |  | 0.0035294 | identifies cell for keyed data entry
4 | 6845146 | 2.88 | 4.9 | 1.6 | 0.00 | 0 | 2000 | CLEAR | 41.5 | 0.3 | [5 empty] | 6.92 | 7.07 | 6.94 | 10.4 | 10.2 | 10.9 |  | 5 | 0.01 | 0 | 4
5 | 6848545 | 3.399 | 5.4 | 1.6 | 0.00 | 0 | 1000 | RAIN | 31.5 | 0.31 |  |  | F | F | F | 6.52 | 6.79 | 6.7 | 10.2 | 8.8 | 9.6 |  | 6 | 0.5 | 0 | 5 |  | 196 | 5556.1414 |  |  | 16 | 453.5626 | 13 | 176 | 4989.1882 |  |  | 20 | 566.9532 | [25 empty] | Week 3 | 14.6667 | 514.578 | 15 | 521.1944 |  | 0.0071429
6 | 6852169 | 3.624 | 5 | 1.6 | 0.00 | 0 | 0 | CLEAR | 32.2 | 0.4 | [5 empty] | 6.82 | 6.91 | 6.78 | 9.9 | 9.2 | 9 |  | 6.5 | 0.3 | 0 | 6 |  | 178 | 5379.9005 |  |  | 18 | 544.0349 | 12 | 182 | 5500.7971 |  |  | 21 | 634.7074 |  | 29733 | 5 | 2 | 12.4 | 33 | 12 | 960 | 12.37 | 12 | EGYPT | STORE |  | pH | Reporting : | - | - | - | 6.11 | - | 7.07 | (s.u.) | 0 | 01/01 | GR
7 | 6855669 | 3.5 | 4.8 | 2 | 0.00 | 3000 | 1000 | CLEAR | 35.4 | 0.14 |  |  | F | F | F | 6.23 | 6.34 | 6.33 | 9.8 | 10.4 | 10.8 |  | 4 | 0.01 | 0 | 7 |  | 160 | 4670.4 | 125 | 3648.75 | 16 | 467.04 | 12 | 176 | 5137.44 | 58 | 1693.02 | 17 | 496.23 | [13 empty] | Effluent | Permit : | - | - | - | 6 | - | 8.5 | (s.u.) | - | 01/01 | GR | Week 4 | 10.3333 | 357.4274 | 13 | 447.1769 |  | 0.0014286
8 | 6859162 | 3.493 | 9 | 1.8 | 0.00 | 0 | 0 | CLOUDY | 37.1 | 1.4 | [5 empty] | 6.12 | 6.59 | 6.53 | 9.8 | 9.2 | 10.4 |  | 2 | 0 | 0 | 8
9 | 6864153 | 4.991 | 6.4 | 2.8 | 0.00 | 0 | 0 | CLOUDY | 30.8 | 0.02 | [5 empty] | 5.9 | 6.15 | 6.37 | 9.6 | 9.5 | 9.1 |  | 2 | 0.01 | 0 | 9 | [39 empty] | Week 5 | [5 empty] | 0.0014286
10 | 6869177 | 5.024 | 5.8 | 2.3 | 0.00 | 200 | 2000 | CLEAR | 23 | 0 | [5 empty] | 6.58 | 6.75 | 6.87 | 10.3 | 9.3 | 9.2 |  | 2 | 0.01 | 0.01 | 10 | [15 empty] | 54636 | 4 | 3.75 | 27.9 | 34 | 24 | 1800 | 12.33 | 24 | EGYPT | STORE
11 | 6873646 | 4.469 | 5.7 | 2 | 0.00 | 300 | 1750 | CLEAR | 25.9 | 0 |  |  | F | F | F | 6.66 | 6.79 | 6.82 | 9.7 | 7.7 | 7.6 |  | 4 | 0.01 | 0 | 11 | [27 empty] | TSS | Reporting : | 532.9413 | 647.626 | (lbs / day) | 16.4167 | 19.3333 | 21 | (mg / L) | 0 | 03/07 | 24
12 | 6877733 | 4.087 | 5.2 | 2 | 0.00 | 0 | 2000 | LT SNOW | 33.7 | 0.1 | [5 empty] | 6.61 | 6.55 | 6.61 | 9.7 | 8.9 | 9 |  | 3.5 | 0.01 | 0.01 | 12 |  | 125 | 4260.6975 |  |  | 15 | 511.2837 | 12 | 104 | 3544.9003 |  |  | 19 | 647.626 |  | 33002 | 5 | 1.75 | 12.4 | 30 | 11 |  |  | 11 | Hawk Ridge | COMPOST |  | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24 | Maximum | 16.6667 | 514.578 | 19.3333 | 597.4303 |  | 0.0071429
13 | 6881688 | 3.955 | 5.4 | 1.8 | 0.00 | 1000 | 1000 | CLEAR | 28.9 | 0 |  |  | O | O | O | 6.34 | 6.53 | 6.59 | 8.9 | 8.4 | 8.5 |  | 3 | 0.01 | 0.01 | 13 |  | 119 | 3925.1793 |  |  | 14 | 461.7858 | 11 | 106 | 3496.3782 |  |  | 18 | 593.7246
14 | 6885358 | 3.67 | 5 | 1.8 | 0.00 | 0 | 500 | CLOUDY | 38.2 | 0 | [5 empty] | 6.56 | 6.69 | 6.63 | 10.2 | 9.3 | 9.8 |  | 3.5 | 0.1 | 0.01 | 14 |  | 135 | 4132.053 | 81 | 2479.2318 | 13 | 397.9014 | 9 | 115 | 3519.897 | 51 | 1560.9978 | 18 | 550.9404
15 | 6889076 | 3.718 | 5.2 | 1.8 | 0.00 | 0 | 0 | CLOUDY | 33.4 | 0.22 |  |  | R | R | R | 5.92 | 6.09 | 6.15 | 10.1 | 9.5 | 9.9 |  | 1.5 | 0.1 | 0.01 | 15
16 | 6892710 | 3.634 | 5 | 1.8 | 0.00 | 0 | 0 | CLOUDY | 34.7 | 0.01 | [5 empty] | 5.95 | 6.05 | 6.11 | 10.1 | 9.5 | 10.1 |  | 3 | 0.01 | 0 | 16 | [27 empty] | SETTLEABLE
17 | 6896330 | 3.62 | 4.9 | 1.8 | 0.00 | 1200 | 2500 | CLEAR | 33.2 | 0 | [5 empty] | 6.71 | 6.72 | 6.73 | 9.7 | 9.1 | 9 |  | 3.5 | 0.01 | 0 | 17 | [15 empty] | 52306 | 4 | 3 | 15.5 | 31 | 12 | 990 | 12.4 |  |  |  |  | SOLIDS | Reporting : | - | - | - | - | 0.0071429 | 0.01 | (mg / L) | 0 | 01/01 | GR
18 | 6899860 | 3.53 | 4.8 | 1.8 | 0.00 | 0 | 2000 | CLEAR | 32.7 | 0 | [5 empty] | 6.82 | 6.8 | 6.82 | 9.6 | 9.4 | 9.2 |  | 4 | 0.1 | 0 | 18 | [23 empty] | 12 | EGYPT | STORE |  | Effluent | Permit : | - | - | - | - | (Report) | 0.3 | (mg / L) | - | 01/01 | GR
19 | 6903435 | 3.575 | 5.8 | 2.2 | 0.00 | 2500 | 2000 | CLOUDY | 33.8 | 0.41 |  |  | S | S | S | 6.42 | 6.56 | 6.62 | 9.5 | 8.4 | 9 |  | 2.5 | 0.01 | 0 | 19 |  | 107 | 3190.2585 |  |  | 12 | 357.786 | 9 | 115 | 3428.7825 |  |  | 14 | 417.417
20 | 6907509 | 4.074 | 6.4 | 2.8 | 0.00 | 200 | 2000 | CLOUDY | 36.3 | 0.55 | [5 empty] | 6.79 | 6.78 | 6.83 | 9.7 | 8.8 | 9.3 |  | 4.5 | 0.3 | 0.01 | 20 |  | 137 | 4654.8709 |  |  | 15 | 509.6574 | 10 | 128 | 4349.0765 |  |  | 15 | 509.6574 |  | 53553 | 3 | 3.75 | 37.2 | 33 | 24 | 1687.5 | 12.38
21 | 6912279 | 4.77 | 5.6 | 2.4 | 0.00 | 0 | 1000 | CLEAR | 27.9 | 0 |  |  | E | E | E | 6.71 | 6.82 | 6.82 | 9.7 | 8.6 | 8.4 |  | 3.5 | 0.01 | 0 | 21 | * | 105 | 4177.089 |  |  | 17 | 676.2906 | 12 | 92 | 3659.9256 | 25 | 994.545 | 16 | 636.5088 | [9 empty] | 24 | EGYPT | STORE
22 | 6916709 | 4.43 | 5.6 | 2.2 | 0.00 | 0 | 0 | CLEAR | 29.8 | 0 | [5 empty] | 6.22 | 6.37 | 6.51 | 8.3 | 8.1 | 8.1 |  | 2 | 0.01 | 0 | 22 | [27 empty] | FLOW | Reporting : | 3.8578 | 5.024 | (MGD) | - | - | - | - | 1 | 99/99 | RC |  |  |  | CBOD
23 | 6920833 | 4.124 | 5.4 | 2 | 0.00 | 0 | 0 | CLEAR | 29.6 | 0 |  |  | A | A | A | 6.48 | 6.67 | 6.73 | 9.2 | 8.5 | 9.1 |  | 1 | 0.01 | 0 | 23 | [27 empty] | Effluent | Permit : | 3.85 | (Report) | (MGD) | - | - | - | - | - | 99/99 | RC
24 | 6924783 | 3.95 | 5.6 | 2 | 0.00 | 6000 | 1000 | CLEAR | 28.3 | 0 | [5 empty] | 6.69 | 6.71 | 6.76 | 9.8 | 8.5 | 8.6 |  | 2.5 | 0.1 | 0 | 24 | [15 empty] | 62410 | 4 | 4 | 27.9 | 33 | 24 | 1800 | 12.4 | [19 empty] | % Removal
25 | 6928772 | 3.989 | 5.4 | 2 | 0.00 | 1200 | 1000 | CLEAR | 28.5 | 0 | 4 |  | S | S | S | 6.82 | 6.87 | 6.86 | 10.3 | 8.5 | 8.4 |  | 4.5 | 0.1 | 0 | 25 | [23 empty] | 24 | EGYPT | STORE
26 | 6932725 | 3.953 | 5.4 | 2.2 | 0.00 | 3300 | 4500 | CLOUDY | 41.9 | 0.06 | [5 empty] | 6.22 | 6.35 | 6.44 | 9.9 | 8.7 | 9.5 |  | 3 | 0.1 | 0.01 | 26 |  | 98 | 3230.866 |  |  | 8 | 263.7442 | 8 | 112 | 3692.4182 |  |  | 15 | 494.5203 | [28 empty] | 92.293
27 | 6936898 | 4.173 | 5.5 | 2.3 | 0.00 | 6000 | 5000 | CLEAR | 37.8 | 0 |  |  | O | O | O | 6.78 | 6.73 | 6.78 | 9.8 | 8.9 | 9.5 |  | 5.5 | 0.01 | 0 | 27 |  | 133 | 4628.7751 |  |  | 12 | 417.6338 | 10 | 127 | 4419.9581 |  |  | 8 | 278.4226 |  | 42063 | 3 | 3 | 24.8 | 31 | 17 | 1170 | 12.35 |  |  |  |  | BOD, 5-day | Reporting : | - | - | - | 89.6434 | - | - | (percent) | 0 | 01/30 | CA
28 | 6941159 | 4.261 | 5.4 | 2.1 | 0.00 | 3000 | 0 | LT SNOW | 33.1 | 0.27 | [5 empty] | 6.76 | 6.73 | 6.68 | 9.9 | 9 | 9.3 |  | 4 | 0.1 | 0 | 28 | ** | 136 | 4832.9966 |  |  | 11 | 390.9041 | 8 | 152 | 5401.5845 |  |  | 16 | 568.5878 | [9 empty] | 17 | EGYPT | STORE |  | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
29 | 6945326 | 4.167 | 5.5 | 2.1 | 0.00 | 0 | 0 | CLEAR | 27.9 | 0.07 |  |  | N | N | N | 6.67 | 6.7 | 6.71 | 9.7 | 7.6 | 8.1 |  | 2.5 | 0.01 | 0 | 29
30 | 6949308 | 3.982 | 5.4 | 2 | 0.00 | 0 | 0 | CLEAR | 33.4 | 0.05 | [5 empty] | 6.75 | 6.7 | 6.77 | 9.5 | 8.1 | 6.7 |  | 1.5 | 0.1 | 0 | 30
31 | 6953188 | 3.88 | 5.8 | 2.1 | 0.00 | 0 | 5500 | LT RAIN | 34 | 0.29 | [5 empty] | 6.79 | 6.83 | 6.82 | 9.8 | 9.1 | 9.6 |  | 4 | 0.1 | 0 | 31
[54 empty] | TSS | Reporting : | - | - | - | 87.571 | - | - | (percent) | 0 | 01/30 | CA
Total | 119593 | 119.593 | - | - | 0 | 27900 | 39750 | - | - | 5.1 | 4 |  | 0 | - | - | - | - | - | - | - | - |  | - | - | - | Total |  | - | - | - | - | - | - | - | - | - | - | - | - | - |  | 379520 | - | 24.5 | 186 | - | 148 | 9967.5 | - | 148 | - | - |  | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
Maximum | - | 5.024 | 9 | 2.8 | 0 | 6000 | 5500 | - | 41.9 | 1.4 | - |  | - | - | - | 6.92 | 7.4 | 7.07 | 10.6 | 10.4 | 10.9 |  | 6.5 | 0.5 | 0.01 | Maximum |  | 196 | 5556.1414 | 125 | 3648.75 | 18 | 676.2906 | 13 | 182 | 5500.7971 | 58 | 1693.02 | 21 | 647.626 |  | - | 5 | - | - | 34 | - | - | 12.4 | - | - | -
Minimum | - | 2.838 | 4.4 | 1 | 0 | 0 | 0 | - | 23 | 0 | - |  | - | - | - | 5.9 | 6.05 | 6.11 | 8.3 | 7.6 | 6.7 |  | 1 | 0 | 0 | Minimum |  | 98 | 3190.2585 | 81 | 2479.2318 | 8 | 263.7442 | 8 | 92 | 3428.7825 | 25 | 994.545 | 8 | 278.4226 |  | - | 3 | - | - | 30 | - | - | 12.33 | - | - | -
Average | - | 3.8578 | 5.4548 | 1.9387 | 0.000 | 900 | 1282.2581 | - | 32.2323 | 0.16452 | - |  | - | - | - | 6.5268 | 6.6606 | 6.6668 | 9.7774 | 8.8871 | 9.0968 |  | 3.4194 | 0.079355 | 0.0025806 | Average |  | 135.75 | 4386.6023 | 103 | 3063.9909 | 13.9167 | 454.302 | 10.5 | 132.0833 | 4261.6955 | 44.6667 | 1416.1876 | 16.4167 | 532.9413 |  | 47440 | 4 | 3.0625 | 23.25 | 32.25 | 18.5 | 1423.9286 | 12.3757 | 18.5 | - | -
[13 empty] | Geometric Mean : |  | - | [15 empty] | Percent Removal : |  | 89.6434 |  |  |  | Percent Removal : |  | 87.571
[27 empty] | * | Primary did not deplete >2.0 mg/L
[27 empty] | ** | Primary sampler malfunctioned

## Graph Mar08
Plant Capacity
3.85 mgd

## April 08
BRUNSWICK SEWER DISTRICT | [12 empty] | State Discharge License Number W 002600-5L-C-R | [9 empty] | Certifying Official: |  |  | Francis E. McVey | BRUNSWICK SEWER DISTRICT | [13 empty] | State Discharge License Number W 002600-5L-C-R | [11 empty] | BRUNSWICK SEWER DISTRICT | [9 empty] | State Discharge License Number W 002600-5L-C-R
Monthly Report of Treatment Operations : | [5 empty] | April | 2008 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [12 empty] | General Manager | Monthly Report of Treatment Operations : |  |  |  |  | April | 2008 | [7 empty] | N.P.D.E.S. Permit Number ME 0100102 | [9 empty] | Page 2. |  | Monthly Report of Treatment Operations : |  |  | April | 2008 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [7 empty] | Page 3.
SETTLEABLE
|  | FLOW | [6 empty] | WEATHER |  |  |  |  | DISINFECTION |  |  | pH. |  |  | TEMPERATURE |  |  |  | SOLIDS |  |  |  | BIOCHEMICAL OXYGEN DEMAND | [6 empty] | TOTAL SUSPENDED SOLIDS | [6 empty] | SLUDGE DEWATERING | [7 empty] | SLUDGE UTILIZATION |  |  |  | SUMMARY DATA | [11 empty] | HIGH WEEKLY AVERAGE VALUES
|  |  | Total | Maxim. | Minim. | [8 empty] | Hypo - | [37 empty] | Stored |  |  |  | LOADING |  |  | CONCENTRATION |  |  |  | REPORTING |  |  |  | BOD |  | TSS |  |  | SETTLEABLE SOLIDS
|  | Totalizer | Flow | Flow | Flow | Flow | Holding | Septic |  | Average | Total | Grit |  | chlorite | Chlorine | [18 empty] | CBOD | [7 empty] | Quantity | Feed | Filter |  | Cake | Sludge | Lime | Average | Quantity |  | or |  |  |  | Monthly | Daily |  | Mo Aver | High Wkly | Daily |  |  |  | Sample
Date |  | Reading | Treated | (instant.) | (instant.) | By-passed | Received | Added | Conditions | Temp. | Precip. | Removed |  | Used | Residual | E. Coli | Influent | Primary | Effluent | Influent | Primary | Effluent |  | Influent | Primary | Effluent | Date | Influent | Influent | Primary | Primary | Effluent | Effluent | Effluent | Influent | Influent | Primary | Primary | Effluent | Effluent |  | Dewatered | Solids | Operation | Polymer | Dry Solid | Dewatered | Added | pH | Utilized | Site | Spread |  |  |  | Average | Maximum | Units | Minimum | Average | Maximum | Units | Exceptions | Frequency | Type |  | High Weekly Average |  | High Weekly Average |  |  | High Weekly Average
|  |  | (MG) | (MG) | (MG) | (MG) | (gallons) | (gallons) |  | (deg. F.) | (inches) | (cu. yd.) |  | (gallons) | (mg/L) | (#/100) | (s.u.) | (s.u.) | (s.u.) | (deg. C.) | (deg. C.) | (deg. C.) |  | (ml/L) | (ml/L) | (ml/L) |  | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) |  | (gallons) | (%) | (hours) | (lbs) | (%) | (cu. yd.) | (lbs) | (s.u.) | (cu. yd.) | [16 empty] | (mg / L) | (lbs / day) | (mg / L) | (lbs / day) |  | (mg / L)
6953188
1 |  | 6957274 | 4.086 | 6.2 | 2.8 | 0.00 | 0 | 0 | LT RAIN | 44.7 | 0.19 | [5 empty] | 6.9 | 6.78 | 6.76 | 9.4 | 9.3 | 9.7 |  | 7.5 | 0.01 | 0 | 1 | [26 empty] | BOD, 5-day | Reporting : | 432.5676 | 1011.175 | (lbs / day) | 11.7692 | 13 | 17 | (mg / L) | 0 | 03/07 | 24 | Week 1 | 10.6667 | 405.7243 | 14.6667 | 558.0683 |  | 0 | check formulas for designation of weeks
2 |  | 6961753 | 4.479 | 6 | 2.6 | 0.00 | 4900 | 1000 | CLEAR | 38.7 | 0.01 | [5 empty] | 6.63 | 6.62 | 6.54 | 10.3 | 9.5 | 9.9 |  | 3 | 0.01 | 0 | 2 | 142 | 5304.3901 |  |  | 11 | 410.9035 | 8 | 117 | 4370.5186 |  |  | 16 | 597.6778 |  | 79084 | 2 | 4.75 | 34.1 | 29 | 24 | 1995 | 12.28 |  |  |  |  | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24
3 |  | 6966408 | 4.655 | 5.8 | 2.3 | 0.00 | 200 | 5000 | CLEAR | 40.6 | 0 |  |  | O | O | O | 6.86 | 6.8 | 6.86 | 9.2 | 9.1 | 9.6 |  | 4 | 0.01 | 0.01 | 3 | 83 | 3222.2841 |  |  | 9 | 349.4043 | 7 | 96 | 3726.9792 |  |  | 14 | 543.5178 | [9 empty] | 24 | EGYPT | STORE | [13 empty] | Week 2 | 13 | 479.4221 | 10.3333 | 381.644 |  | 0.0014286 | identifies cell for keyed data entry
4 |  | 6970973 | 4.565 | 5.6 | 2.9 | 0.00 | 0 | 2000 | CLOUDY | 38.1 | 0.55 | [5 empty] | 6.74 | 6.73 | 6.69 | 9.8 | 9 | 9.6 |  | 3 | 0.01 | 0 | 4 | 133 | 5063.5893 | 61 | 2322.3981 | 12 | 456.8652 | 9 | 105 | 3997.5705 | 34 | 1294.4514 | 14 | 533.0094
5 |  | 6975840 | 4.867 | 6 | 2.8 | 0.00 | 0 | 0 | RAIN | 40.9 | 0.03 |  |  | F | F | F | 6.9 | 6.85 | 6.77 | 9.4 | 8.9 | 9.4 |  | 2 | 0.01 | 0 | 5 | [38 empty] | Week 3 | 11 | 354.6057 | 12.6667 | 407.8594 |  | 0
6 | * | 6980695 | 4.855 | 6.1 | 2.6 | 0.00 | 0 | 0 | CLOUDY | 39.4 | 0 | [5 empty] | 6.94 | 6.9 | 6.8 | 9.4 | 8.9 | 9.8 |  | 2 | 0.01 | 0 | 6 | [26 empty] | pH | Reporting : | - | - | - | 6.07 | - | 6.95 | (s.u.) | 0 | 01/01 | GR
7 |  | 6985389 | 4.694 | 6.1 | 2.6 | 0.00 | 2000 | 3750 | CLEAR | 38.2 | 0 |  |  | F | F | F | 6.73 | 6.13 | 6.45 | 10 | 9.3 | 9.6 |  | 4 | 1.5 | 0 | 7 | [14 empty] | 70991 | 2 | 4.75 | 40.3 | 30 | 21 |  |  | 21 | Hawk Ridge | COMPOST |  | Effluent | Permit : | - | - | - | 6 | - | 8.5 | (s.u.) | - | 01/01 | GR | Week 4 | 10.6667 | 297.649 | 14 | 390.6567 |  | 0.0014286
8 |  | 6989996 | 4.607 | 6 | 2.3 | 0.00 | 8000 | 4000 | CLEAR | 39.1 | 0 | [5 empty] | 6.77 | 6.76 | 6.88 | 10.6 | 9.3 | 10.5 |  | 4 | 0.01 | 0 | 8
9 |  | 6994490 | 4.494 | 6.2 | 2.3 | 0.00 | 6000 | 3000 | CLEAR | 40 | 0 | [5 empty] | 6.72 | 6.68 | 6.69 | 10.1 | 9.4 | 10 |  | 2 | 0.01 | 0 | 9 | 128 | 4797.4349 |  |  | 11 | 412.2796 | 8 | 118 | 4422.6353 |  |  | 9 | 337.3196 | [25 empty] | Week 5
10 |  | 6998923 | 4.433 | 6.1 | 2.2 | 0.00 | 4100 | 10000 | CLEAR | 51.2 | 0.02 | [5 empty] | 6.83 | 6.69 | 6.63 | 9.7 | 9.3 | 10 |  | 3.5 | 0.01 | 0 | 10 | 120 | 4436.5464 |  |  | 12 | 443.6546 | 8 | 106 | 3918.9493 |  |  | 12 | 443.6546 |  | 33590 | 2 | 3.75 | 18.6 | 30 | 11 |  |  | 11 | Hawk Ridge | COMPOST
11 |  | 7003287 | 4.364 | 5.6 | 2.4 | 0.00 | 7500 | 12500 | CLEAR | 44.9 | 0.09 |  |  | F | F | F | 6.88 | 6.86 | 6.79 | 10.1 | 9.3 | 10.1 |  | 7 | 0.01 | 0.01 | 11 | 130 | 4731.4488 | 80 | 2911.6608 | 16 | 582.3322 | 11 | 167 | 6078.0919 | 35 | 1273.8516 | 10 | 363.9576 | [13 empty] | TSS | Reporting : | 506.365 | 1368.0602 | (lbs / day) | 13.6923 | 14.6667 | 23 | (mg / L) | 0 | 03/07 | 24
12 |  | 7007641 | 4.354 | 5.8 | 2.3 | 0.00 | 0 | 0 | RAIN | 43.3 | 0.39 | [5 empty] | 6.95 | 6.91 | 6.73 | 9.6 | 9 | 9.8 |  | 2.5 | 0.01 | 0 | 12 | [26 empty] | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24 | Maximum | 13 | 479.4221 | 14.6667 | 558.0683 |  | 0.0014286
13 |  | 7012080 | 4.439 | 5.6 | 2.1 | 0.00 | 2900 | 1000 | CLEAR | 41.4 | 0 |  |  | O | O | O | 6.94 | 6.78 | 6.76 | 11 | 12.1 | 11.8 |  | 2 | 0.01 | 0 | 13
14 |  | 7016337 | 4.257 | 5.8 | 2 | 0.00 | 7500 | 3000 | CLEAR | 41 | 0 | [5 empty] | 6.9 | 6.83 | 6.86 | 10 | 9.2 | 10.6 |  | 4 | 0.01 | 0 | 14 | [14 empty] | 60867 | 1 | 4 | 31 | 26 | 22 |  |  | 22 | Hawk Ridge | COMPOST
15 |  | 7020409 | 4.072 | 5.2 | 1.9 | 0.00 | 2700 | 7750 | CLEAR | 43.4 | 0 |  |  | R | R | R | 6.86 | 6.84 | 6.77 | 10.6 | 9.4 | 10 |  | 6 | 0.01 | 0 | 15
16 |  | 7024353 | 3.944 | 5.6 | 2 | 0.00 | 0 | 10000 | CLEAR | 44.2 | 0 | [5 empty] | 6.82 | 6.67 | 6.65 | 10.4 | 9.9 | 10.3 |  | 4 | 0.01 | 0 | 16 | 164 | 5394.4454 |  |  | 11 | 361.8226 | 8 | 145 | 4769.4792 |  |  | 11 | 361.8226 | [13 empty] | SETTLEABLE
17 |  | 7028205 | 3.852 | 5.4 | 1.8 | 0.00 | 1200 | 11000 | CLEAR | 46.1 | 0 | [5 empty] | 6.83 | 6.77 | 6.67 | 10.4 | 10.7 | 10.4 |  | 3.5 | 0.01 | 0 | 17 | 100 | 3212.568 |  |  | 11 | 353.3825 | 7 | 136 | 4369.0925 |  |  | 14 | 449.7595 |  | 35388 | 2 | 2 | 21.7 | 26 | 11 |  |  | 11 | Hawk Ridge | COMPOST |  | SOLIDS | Reporting : | - | - | - | - | 0.0014286 | 0.1 | (mg / L) | 0 | 01/01 | GR
18 |  | 7032005 | 3.8 | 6.4 | 1.8 | 0.00 | 1000 | 4750 | CLEAR | 55.9 | 0 | [5 empty] | 6.69 | 6.74 | 6.68 | 10.9 | 10.6 | 11.3 |  | 5 | 0.1 | 0 | 18 | 133 | 4215.036 | 89 | 2820.588 | 11 | 348.612 | 7 | 147 | 4658.724 | 43 | 1362.756 | 13 | 411.996 | [13 empty] | Effluent | Permit : | - | - | - | - | (Report) | 0.3 | (mg / L) | - | 01/01 | GR
19 |  | 7035775 | 3.77 | 5.2 | 1.6 | 0.00 | 5200 | 1000 | CLEAR | 51.3 | 0 |  |  | S | S | S | 5.76 | 6.02 | 6.07 | 10.7 | 10.3 | 11.2 |  | 3 | 0.01 | 0 | 19
20 |  | 7039278 | 3.503 | 5 | 1.6 | 0.00 | 0 | 4000 | CLEAR | 46.7 | 0 | [5 empty] | 6.07 | 6.38 | 6.39 | 10.8 | 10.3 | 10.9 |  | 2.5 | 0.1 | 0 | 20
21 |  | 7042739 | 3.461 | 5 | 1.6 | 0.00 | 200 | 4000 | CLEAR | 47.7 | 0 |  |  | E | E | E | 5.96 | 6.08 | 6.15 | 10.6 | 10.3 | 11.2 |  | 4 | 0.1 | 0.01 | 21
22 |  | 7046185 | 3.446 | 5 | 1.6 | 0.00 | 900 | 8000 | CLEAR | 51.4 | 0 | [5 empty] | 7.04 | 6.88 | 6.87 | 11.3 | 11.3 | 12 |  | 4.5 | 0.01 | 0 | 22 | [14 empty] | 68867 | 3 | 4.25 | 31 | 30 | 22 |  |  | 22 | Hawk Ridge | COMPOST |  | FLOW | Reporting : | 4.1133 | 7.132 | (MGD) | - | - | - | - | 1 | 99/99 | RC |  |  |  | CBOD
23 |  | 7049538 | 3.353 | 5.2 | 1.4 | 0.00 | 3400 | 5750 | CLEAR | 58.5 | 0 |  |  | A | A | A | 6.8 | 6.87 | 6.67 | 10.1 | 10.4 | 11.5 |  | 4 | 0.01 | 0 | 23 | 123 | 3439.5745 |  |  | 13 | 363.5323 | 8 | 146 | 4082.7469 |  |  | 16 | 447.4243 | [13 empty] | Effluent | Permit : | 3.85 | (Report) | (MGD) | - | - | - | - | - | 99/99 | RC
24 |  | 7052989 | 3.451 | 4.8 | 1.4 | 0.00 | 2700 | 4000 | CLEAR | 59.6 | 0 | [5 empty] | 6.87 | 6.86 | 6.57 | 11.1 | 11.4 | 12.8 |  | 5 | 0.01 | 0 | 24 | 149 | 4288.4197 |  |  | 8 | 230.2507 | 6 | 182 | 5238.2039 |  |  | 11 | 316.5947 |  | 23071 | 4 | 1.75 | 15.5 | 29 | 11 |  |  | 11 | Hawk Ridge | COMPOST | [16 empty] | % Removal
25 |  | 7056250 | 3.261 | 4.6 | 1.4 | 0.00 | 5200 | 9250 | CLEAR | 49.3 | 0 |  |  | S | S | S | 6.97 | 6.88 | 6.61 | 11.6 | 11 | 12.2 |  | 6 | 0.01 | 0 | 25 | 169 | 4596.2491 | 84 | 2284.5262 | 11 | 299.1641 | 8 | 158 | 4297.0849 | 40 | 1087.8696 | 15 | 407.9511 |  | 17236 | 4 | 2 | 12.4 | 27 | 12 |  |  | 12 | Hawk Ridge | COMPOST
26 |  | 7059407 | 3.157 | 4.7 | 1.2 | 0.00 | 0 | 3000 | CLEAR | 46.5 | 0 | [5 empty] | 6.59 | 6.62 | 6.72 | 11 | 11 | 11.8 |  | 3.5 | 0.01 | 0 | 26 | [41 empty] | 93.5346
27 |  | 7062449 | 3.042 | 4.5 | 1.1 | 0.00 | 0 | 0 | CLOUDY | 46.3 | 0.01 |  |  | O | O | O | 6.54 | 6.64 | 6.63 | 10.4 | 10.6 | 11.5 |  | 5 | 0.01 | 0 | 27 | [26 empty] | BOD, 5-day | Reporting : | - | - | - | 90.2839 | - | - | (percent) | 0 | 01/30 | CA
28 |  | 7065474 | 3.025 | 7.2 | 2 | 0.00 | 3200 | 5750 | CLOUDY | 44.4 | 1.25 | [5 empty] | 6.89 | 6.76 | 6.86 | 11.6 | 11.7 | 12.5 |  | 5 | 0.01 | 0 | 28 | [14 empty] | 33927 | 3 | 2.5 | 18.6 | 28 | 11 |  |  | 11 | Hawk Ridge | COMPOST |  | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
29 |  | 7069456 | 3.982 | 9 | 4.8 | 0.00 | 3300 | 6500 | RAIN | 46.9 | 2.95 |  |  | N | N | N | 6.94 | 6.87 | 6.81 | 10.9 | 10.8 | 11.6 |  | 13 | 0.4 | 0.1 | 29 | [14 empty] | 19781 | 5 | 2 | 12.4 | 28 | 12 |  |  | 12 | Hawk Ridge | COMPOST
30 |  | 7076588 | 7.132 | 8.2 | 3.6 | 0.00 | 200 | 4000 | CLEAR | 42.4 | 0 | [5 empty] | 6.72 | 6.74 | 6.95 | 10.7 | 10.4 | 11 |  | 3.5 | 0.3 | 0.01 | 30 | 87 | 5174.8366 |  |  | 17 | 1011.175 | 14 | 81 | 4817.9513 |  |  | 23 | 1368.0602
31 | [26 empty] | 31
[54 empty] | TSS | Reporting : | - | - | - | 89.554 | - | - | (percent) | 0 | 01/30 | CA
Total |  | 123400 | 123.4 | - | - | 0 | 72300 | 134000 | - | - | 5.49 | 0.0 |  | 0 | - | - | - | - | - | - | - | - |  | - | - | - | Total | - | - | - | - | - | - | - | - | - | - | - | - | - |  | 442802 | - | 31.75 | 235.6 | - | 157 | 1995 | - | 157 | - | - |  | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
Maximum |  | - | 7.132 | 9 | 4.8 | 0 | 8000 | 12500 | - | 59.6 | 2.95 | - |  | - | - | - | 7.04 | 6.91 | 6.95 | 11.6 | 12.1 | 12.8 |  | 13 | 1.5 | 0.1 | Maximum | 169 | 5394.4454 | 89 | 2911.6608 | 17 | 1011.175 | 14 | 182 | 6078.0919 | 43 | 1362.756 | 23 | 1368.0602 |  | - | 5 | - | - | 30 | - | - | 12.28 | - | - | -
Minimum |  | - | 3.025 | 4.5 | 1.1 | 0 | 0 | 0 | - | 38.1 | 0 | - |  | - | - | - | 5.76 | 6.02 | 6.07 | 9.2 | 8.9 | 9.4 |  | 2 | 0.01 | 0 | Minimum | 83 | 3212.568 | 61 | 2284.5262 | 8 | 230.2507 | 6 | 81 | 3726.9792 | 34 | 1087.8696 | 9 | 316.5947 |  | - | 1 | - | - | 26 | - | - | 12.28 | - | - | -
Average |  | - | 4.1133 | 5.7967 | 2.1667 | 0.000 | 2410 | 4466.6667 | - | 45.4033 | 0.183 | - |  | - | - | - | 6.7347 | 6.698 | 6.676 | 10.39 | 10.0567 | 10.7533 |  | 4.2667 | 0.091333 | 0.0046667 | Average | 127.7692 | 4452.0633 | 78.5 | 2584.7933 | 11.7692 | 432.5676 | 8.3846 | 131.0769 | 4519.079 | 38 | 1254.7322 | 13.6923 | 506.365 |  | 44280.2 | 2.8 | 3.175 | 23.56 | 28.3 | 15.7 | 1995 | 12.28 | 15.7 | - | -
[14 empty] | Geometric Mean : |  | - | [14 empty] | Percent Removal : |  | 90.2839 |  |  |  | Percent Removal : |  | 89.554
| * | In taking Plant flow readings for 06 April 2008, minimum and maximum flow values for the day were unavailable due to a chart drive failure. The flow totalizer reading was unaffected by the failure, and the value reported for total flow treated is valid.
Minimum and maximum flow values for 06 April 2008 have been estimated and are stated as the more conservative of similar values for the day before and the day following the day of the drive failure.
Totalizer OK/ Chart drive failure no min/max

## Graph Apr08
Plant Capacity
3.85 mgd

## May 08
BRUNSWICK SEWER DISTRICT | [11 empty] | State Discharge License Number W 002600-5L-C-R | [9 empty] | Certifying Official: |  |  | Francis E. McVey | BRUNSWICK SEWER DISTRICT | [13 empty] | State Discharge License Number W 002600-5L-C-R | [11 empty] | BRUNSWICK SEWER DISTRICT | [9 empty] | State Discharge License Number W 002600-5L-C-R
Monthly Report of Treatment Operations : |  |  |  |  | May | 2008 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [12 empty] | General Manager | Monthly Report of Treatment Operations : |  |  |  |  | May | 2008 | [7 empty] | N.P.D.E.S. Permit Number ME 0100102 | [9 empty] | Page 2. |  | Monthly Report of Treatment Operations : |  |  | May | 2008 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [7 empty] | Page 3.
SETTLEABLE
| FLOW | [6 empty] | WEATHER |  |  |  |  | DISINFECTION |  |  | P.H. |  |  | TEMPERATURE |  |  |  | SOLIDS |  |  |  | BIOCHEMICAL OXYGEN DEMAND | [6 empty] | TOTAL SUSPENDED SOLIDS | [6 empty] | SLUDGE DEWATERING | [7 empty] | SLUDGE UTILIZATION |  |  |  | SUMMARY DATA | [11 empty] | HIGH WEEKLY AVERAGE VALUES
|  | Total | Maxim. | Minim. | [8 empty] | Hypo - | [37 empty] | Stored |  |  |  | LOADING |  |  | CONCENTRATION |  |  |  | REPORTING |  |  |  | BOD |  | TSS |  |  | SETTLEABLE SOLIDS
| Totalizer | Flow | Flow | Flow | Flow | Holding | Septic |  | Average | Total | Grit |  | chlorite | Chlorine | [18 empty] | CBOD | [7 empty] | Quantity | Feed | Filter |  | Cake | Sludge | Lime | Average | Quantity |  | or |  |  |  | Monthly | Daily |  | Mo Aver | High Wkly | Daily |  |  |  | Sample
Date | Reading | Treated | (instant.) | (instant.) | By-passed | Received | Added | Conditions | Temp. | Precip. | Removed |  | Used | Residual | E. Coli | Influent | Primary | Effluent | Influent | Primary | Effluent |  | Influent | Primary | Effluent | Date | Influent | Influent | Primary | Primary | Effluent | Effluent | Effluent | Influent | Influent | Primary | Primary | Effluent | Effluent |  | Dewatered | Solids | Operation | Polymer | Dry Solid | Dewatered | Added | pH | Utilized | Site | Spread |  |  |  | Average | Maximum | Units | Minimum | Average | Maximum | Units | Exceptions | Frequency | Type |  | High Weekly Average |  | High Weekly Average |  |  | High Weekly Average
|  | (MG) | (MG) | (MG) | (MG) | (gallons) | (gallons) |  | (deg. F.) | (inches) | (cu. yd.) |  | (gallons) | (mg/L) | (#/100) | (s.u.) | (s.u.) | (s.u.) | (deg. C.) | (deg. C.) | (deg. C.) |  | (ml/L) | (ml/L) | (ml/L) |  | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) |  | (gallons) | (%) | (hours) | (lbs) | (%) | (cu. yd.) | (lbs) | (s.u.) | (cu. yd.) | [16 empty] | (mg / L) | (lbs / day) | (mg / L) | (lbs / day) |  | (mg / L)
7076588
1 | 7082758 | 6.17 | 7.8 | 3.5 | 0.00 | 14200 | 11250 | CLEAR | 41.55 | 0 |  |  | OFF FOR SEASON | OFF FOR SEASON | OFF FOR SEASON | 6.8 | 6.78 | 6.74 | 11.2 | 10.8 | 11.2 |  | 5 | 0.01 | 0.1 | 1 | 89 | 4579.7442 |  |  | 11 | 566.0358 | 7 | 72 | 3704.9616 |  |  | 18 | 926.2404 | [13 empty] | BOD, 5-day | Reporting : | 382.0715 | 566.0358 | (lbs / day) | 12.3571 | 13.6667 | 15 | (mg / L) | 0 | 03/07 | 24 | Week 1 | 13 | 674 | 20 | 1031 |  | <0.1 | check formulas for designation of weeks
2 | 7088077 | 5.319 | 7 | 2.2 | 0.00 | 13500 | 6500 | CLEAR | 44.5 | 0 | [5 empty] | 6.65 | 6.68 | 6.74 | 11.5 | 10.8 | 11.6 |  | 4 | 0.1 | 0.1 | 2 | 107 | 4746.5692 | 74 | 3282.674 | 10 | 443.6046 | 7 | 140 | 6210.4644 | 50 | 2218.023 | 18 | 798.4883 |  | 31787 | 4 | 2.25 | 15.5 | 28 | 11 |  |  | 11 | Hawk Ridge | COMPOST |  | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24
3 | 7092938 | 4.861 | 6.3 | 3.4 | 0.00 | 0 | 0 | CLOUDY | 43.6 | 0.39 | [5 empty] | 6.7 | 6.71 | 6.66 | 11.2 | 11 | 11.8 |  | 1 | 0.01 | 0.1 | 3 | [38 empty] | Week 2 | 11 | 395.4661 | 18.3333 | 662.1404 |  | 0.1 | identifies cell for keyed data entry
4 | 7097650 | 4.712 | 6.8 | 3.4 | 0.00 | 0 | 0 | LT RAIN | 43.9 | 0.48 | [5 empty] | 6.81 | 6.79 | 6.77 | 11.1 | 11.1 | 11.8 |  | 1.5 | 0.01 | 0.1 | 4
5 | 7102600 | 4.95 | 6.8 | 3 | 0.00 | 5800 | 9000 | CLEAR | 51.9 | 0 | [5 empty] | 6.79 | 6.7 | 6.69 | 11.7 | 11.7 | 12.1 |  | 2.5 | 0.01 | 0.1 | 5 | [14 empty] | 33746 | 3 | 2.5 | 21.7 | 27 | 11 |  |  | 11 | Hawk Ridge | COMPOST | [13 empty] | Week 3 | 13.3333 | 402.9221 | 18.3333 | 553.6815 |  | 0.1
6 | 7107357 | 4.757 | 6 | 2.4 | 0.00 | 5600 | 5750 | CLEAR | 53 | 0 | [5 empty] | 6.81 | 6.78 | 6.67 | 11.9 | 11.6 | 12.6 |  | 4.5 | 0.01 | 0.1 | 6 | [14 empty] | 18284 | 4 | 1.5 | 12.4 | 30 | 11 |  |  | 11 | Hawk Ridge | COMPOST |  | pH | Reporting : | - | - | - | 6.12 | - | 6.9 | (s.u.) | 0 | 01/01 | GR
7 | 7111860 | 4.503 | 5.8 | 2.2 | 0.00 | 0 | 8250 | CLEAR | 58 | 0 | [5 empty] | 6.78 | 6.7 | 6.51 | 12.4 | 14.4 | 14.5 |  | 5 | 0.01 | 0.1 | 7 | 102 | 3830.612 |  |  | 8 | 300.4402 | 5 | 119 | 4469.0474 |  |  | 20 | 751.1004 | [13 empty] | Effluent | Permit : | - | - | - | 6 | - | 8.5 | (s.u.) | - | 01/01 | GR | Week 4 | 12.6667 | 326.9224 | 24 | 619.3451 |  | 0.1
8 | 7116221 | 4.361 | 5.4 | 2.1 | 0.00 | 4100 | 10750 | RAIN | 60.8 | 0.04 | [5 empty] | 6.82 | 6.74 | 6.62 | 12 | 11.6 | 12.7 |  | 6.5 | 0.1 | 0.1 | 8 | 158 | 5746.5769 |  |  | 12 | 436.4489 | 7 | 176 | 6401.2502 |  |  | 14 | 509.1904 |  | 30064 | 4 | 2.25 | 15.5 | 27 | 11 |  |  | 11 | Hawk Ridge | COMPOST
9 | 7120367 | 4.146 | 5.8 | 2 | 0.00 | 1400 | 12000 | CLEAR | 53.5 | 0 | [5 empty] | 6.75 | 6.7 | 6.6 | 11.6 | 11.8 | 12.9 |  | 4 | 0.1 | 0.1 | 9 | 139 | 4806.292 | 87 | 3008.2547 | 13 | 449.5093 | 9 | 176 | 6085.6646 | 65 | 2247.5466 | 21 | 726.1304 |  | 16510 | 5 | 2 | 12.4 | 29 | 11 |  |  | 11 | Hawk Ridge | COMPOST | [13 empty] | Week 5 | 13.6667 | 321.1428 | 25 | 586.6634 |  | 0.1
10 | 7124426 | 4.059 | 5.3 | 1.9 | 0.00 | 0 | 0 | CLEAR | 51.8 | 0 | [5 empty] | 6.99 | 6.96 | 6.58 | 11.4 | 11.4 | 12.2 |  | 5 | 0.01 | 0.1 | 10
11 | 7128230 | 3.804 | 5.2 | 1.8 | 0.00 | 0 | 0 | CLEAR | 51.3 | 0 | [5 empty] | 6.97 | 6.86 | 6.71 | 11.4 | 11.2 | 12.1 |  | 1.5 | 0.01 | 0.1 | 11 | [26 empty] | TSS | Reporting : | 642.1586 | 926.2404 | (lbs / day) | 20.9286 | 25 | 27 | (mg / L) | 0 | 03/07 | 24
12 | 7131922 | 3.692 | 5.6 | 1.8 | 0.00 | 4200 | 7500 | CLEAR | 50.8 | 0 | [5 empty] | 6.73 | 6.71 | 6.67 | 11.8 | 11.6 | 12.4 |  | 3 | 0.1 | 0.1 | 12 | [14 empty] | 33129 | 2 | 2 | 15.5 | 28 | 11 |  |  | 11 | Hawk Ridge | COMPOST |  | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24 | Maximum | 13.6667 | 674 | 25 | 1031 |  | 0.1
13 | 7135675 | 3.753 | 6.2 | 1.6 | 0.00 | 2000 | 10750 | CLEAR | 57 | 0 | [5 empty] | 6.86 | 6.8 | 6.58 | 12.6 | 12.4 | 12.9 |  | 7.5 | 0.1 | 0.1 | 13 | [14 empty] | 56525 | 5 | 1.75 | 6.2 | 29 | 11 |  |  | 11 | Hawk Ridge | COMPOST
14 | 7139569 | 3.894 | 5.4 | 1.8 | 0.00 | 2300 | 8000 | CLEAR | 53.4 | 0 | [5 empty] | 6.88 | 7.01 | 6.65 | 12.2 | 11.8 | 12.9 |  | 5 | 0.01 | 0.1 | 14 | 156 | 5066.2498 |  |  | 14 | 454.6634 | 10 | 148 | 4806.4421 |  |  | 19 | 617.0432
15 | 7143034 | 3.465 | 5.2 | 1.6 | 0.00 | 10200 | 10500 | CLOUDY | 52.1 | 0 |  |  | 40.9 | 0.55 | 5.2 | 6.94 | 6.92 | 6.89 | 12.1 | 12.3 | 13.2 |  | 4 | 0.01 | 0.1 | 15 | 188 | 5432.8428 |  |  | 11 | 317.8791 | 8 | 161 | 4652.5941 |  |  | 16 | 462.3696 |  | 33751 | 4 | 3.25 | 40.3 | 26 | 12 |  |  | 12 | Hawk Ridge | COMPOST
16 | 7146521 | 3.487 | 4.8 | 1.6 | 0.00 | 0 | 7750 | CLEAR | 55.2 | 0 |  |  | 34.4 | 0.47 | 35.7 | 6.9 | 6.86 | 6.86 | 12.6 | 12.7 | 13.3 |  | 5 | 0.01 | 0.1 | 16 | 189 | 5496.4186 | 146 | 4245.9107 | 15 | 436.2237 | 12 | 171 | 4972.9502 | 77 | 2239.2817 | 20 | 581.6316 | [13 empty] | SETTLEABLE
17 | 7149824 | 3.303 | 4.8 | 1.6 | 0.00 | 0 | 0 | RAIN | 55 | 0.03 |  |  | 33.4 | 0.45 |  | 7.02 | 6.99 | 6.89 | 12.2 | 12.6 | 13.6 |  | 5 | 0.01 | 0.1 | 17 | [26 empty] | SOLIDS | Reporting : | - | - | - | - | - | 0.1 | (mg / L) | 0 | 01/01 | GR
18 | 7153081 | 3.257 | 4.8 | 1.6 | 0.00 | 1500 | 3800 | RAIN | 56.2 | 0 |  |  | 38.2 | 0.52 |  | 7.09 | 7.08 | 6.68 | 12.6 | 13.1 | 13.9 |  | 3 | 0.01 | 0.1 | 18 | [26 empty] | Effluent | Permit : | - | - | - | - | - | 0.3 | (mg / L) | - | 01/01 | GR
19 | 7156251 | 3.17 | 4.6 | 1.4 | 0.00 | 1200 | 6000 | CLEAR | 52.6 | 0 |  |  | 35.4 | 0.76 | 33.6 | 6.85 | 6.7 | 6.6 | 12.5 | 13.1 | 14 |  | 5 | 0.01 | 0.1 | 19 | [14 empty] | 54309 | 2 | 3.75 | 27.9 | 27 | 25 |  |  | 25 | Hawk Ridge | COMPOST
20 | 7159399 | 3.148 | 4.5 | 1.4 | 0.00 | 2000 | 6750 | CLEAR | 52.5 | 0 |  |  | 35.2 | 0.49 | 7.4 | 6.79 | 6.74 | 6.67 | 12.7 | 12.5 | 13 |  | 4 | 0.2 | 0.1 | 20
21 | 7162533 | 3.134 | 4.6 | 1.2 | 0.00 | 1050 | 11250 | LT RAIN | 53.3 | 0.01 |  |  | 34.1 | 0.55 | 54.6 | 6.92 | 7.02 | 6.45 | 12.7 | 12.6 | 13.7 |  | 6 | 0.2 | 0.1 | 21 | 213 | 5567.3003 |  |  | 12 | 313.6507 | 9 | 274 | 7161.6914 |  |  | 22 | 575.0263
22 | 7165613 | 3.08 | 4.6 | 1.2 | 0.00 | 6700 | 8500 | CLEAR | 52.3 | 0.03 |  |  | 35.7 | 0.49 |  | 6.93 | 7.05 | 6.35 | 13.1 | 12.8 | 14 |  | 6 | 0.2 | 0.1 | 22 | 233 | 5985.1176 |  |  | 11 | 282.5592 | 8 | 260 | 6678.672 |  |  | 23 | 590.8056 |  | 41730 | 4 | 2.75 | 21.7 | 23 | 25 |  |  | 25 | Hawk Ridge | COMPOST |  | FLOW | Reporting : | 3.699 | 6.17 | (MGD) | - | - | - | - | 0 | 99/99 | RC |  |  |  | CBOD
23 | 7168687 | 3.074 | 5 | 1.2 | 0.00 | 11100 | 8000 | CLEAR | 55.1 | 0.01 |  |  | 32.1 | 0.4 |  | 6.88 | 7.09 | 6.5 | 13.1 | 12.7 | 13.6 |  | 5.5 | 0.1 | 0.1 | 23 | 228 | 5845.2725 | 151 | 3871.2112 | 15 | 384.5574 | 10 | 274 | 7024.5818 | 118 | 3025.1849 | 27 | 692.2033 | [13 empty] | Effluent | Permit : | 3.85 | (Report) | (MGD) | - | - | - | - | - | 99/99 | RC
24 | 7171778 | 3.091 | 4.5 | 1.2 | 0.00 | 0 | 0 | CLEAR | 56.2 | 0.01 |  |  | 30.3 | 0.46 |  | 7.09 | 6.97 | 6.9 | 13.3 | 12.7 | 13.7 |  | 6 | 0.1 | 0.1 | 24 | [41 empty] | % Removal
25 | 7174640 | 2.862 | 4.3 | 1.2 | 0.00 | 0 | 0 | CLEAR | 58.8 | 0 |  |  | 27.4 | 0.54 |  | 7.17 | 7.03 | 6.82 | 12.6 | 12.3 | 13.7 |  | 5 | 0.1 | 0.1 | 25
26 | 7177369 | 2.729 | 4.2 | 1 | 0.00 | 0 | 0 | CLEAR | 59.9 | 0.01 |  |  | 25.5 | 0.44 |  | 6.95 | 6.88 | 6.84 | 13.3 | 12.9 | 14.1 |  | 2 | 0.1 | 0.1 | 26 | [41 empty] | 94.8318
27 | 7180149 | 2.78 | 4.8 | 1.1 | 0.00 | 1500 | 7500 | CLEAR | 62.3 | 0.03 |  |  | 28.4 | 0.51 | 1 | 6.95 | 6.76 | 6.87 | 13.7 | 14 | 15.8 |  | 5 | 0.1 | 0.1 | 27 | [26 empty] | BOD, 5-day | Reporting : | - | - | - | 92.7785 | - | - | (percent) | 0 | 01/30 | CA
28 | 7183088 | 2.939 | 4.2 | 1 | 0.00 | 1650 | 4750 | CLEAR | 52.8 | 0 |  |  | 25.7 | 0.44 | 11.7 | 6.77 | 6.69 | 6.32 | 13 | 13.1 | 13 |  | 4 | 0.1 | 0.1 | 28 | 229 | 5613.0785 |  |  | 15 | 367.6689 | 11 | 246 | 6029.77 |  |  | 26 | 637.2928 |  | 45208 | 3 | 3.25 | 24.8 | 25 | 26 |  |  | 26 | Hawk Ridge | COMPOST |  | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
29 | 7185847 | 2.759 | 4.4 | 1 | 0.00 | 7200 | 6500 | CLEAR | 60.1 | 0 |  |  | 29.2 | 0.47 | 1 | 6.95 | 6.84 | 6.37 | 13.5 | 13.7 | 14.1 |  | 6.5 | 0.4 | 0.1 | 29 | 216 | 4970.173 |  |  | 14 | 322.1408 | 11 | 216 | 4970.173 |  |  | 26 | 598.2616 |  | 39860 | 4 | 3 | 21.7 | 22 | 26 |  |  | 26 | Hawk Ridge | COMPOST
30 | 7188581 | 2.734 | 4.7 | 1 | 0.00 | 5700 | 8000 | CLEAR | 55 | 0 |  |  | 28.4 | 0.44 |  | 6.93 | 7.08 | 6.47 | 13.7 | 13.6 | 14.8 |  | 7 | 1 | 0.1 | 30 | 280 | 6384.4368 | 163 | 3716.6543 | 12 | 273.6187 | 10 | 256 | 5837.1994 | 114 | 2599.3778 | 23 | 524.4359 |  | 20453 | 4 | 2 | 12.4 | 23 | 14 |  |  | 14 | Hawk Ridge | COMPOST
31 | 7191257 | 2.676 | 6.4 | 1.1 | 0.00 | 0 | 0 | RAIN | 54.6 | 0.53 |  |  | 28.2 | 0.52 |  | 6.59 | 6.75 | 6.12 | 12.8 | 13.2 | 14.6 |  | 4 | 1 | 0.1 | 31
[53 empty] | TSS | Reporting : | - | - | - | 89.1038 | - | - | (percent) | 0 | 01/30 | CA
Total | 114669 | 114.669 | - | - | 0 | 102900 | 179050 | - | - | 1.57 | 0.0 |  | 542.5 | - | - | - | - | - | - | - | - |  | - | - | - | Total | - | - | - | - | - | - | - | - | - | - | - | - | - |  | 455356 | - | 32.25 | 248 | - | 205 |  | - | 205 | - | - |  | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
Maximum | - | 6.17 | 7.8 | 3.5 | 0 | 14200 | 12000 | - | 62.3 | 0.53 | - |  | - | 0.76 | 54.6 | 7.17 | 7.09 | 6.9 | 13.7 | 14.4 | 15.8 |  | 7.5 | 1 | 0.1 | Maximum | 280 | 6384.4368 | 163 | 4245.9107 | 15 | 566.0358 | 12 | 274 | 7161.6914 | 118 | 3025.1849 | 27 | 926.2404 |  | - | 5 | - | - | 30 | - | - |  | - | - | -
Minimum | - | 2.676 | 4.2 | 1 | 0 | 0 | 0 | - | 41.55 | 0 | - |  | - | 0.4 | 1 | 6.59 | 6.68 | 6.12 | 11.1 | 10.8 | 11.2 |  | 1 | 0.01 | 0.1 | Minimum | 89 | 3830.612 | 74 | 3008.2547 | 8 | 273.6187 | 5 | 72 | 3704.9616 | 50 | 2218.023 | 14 | 462.3696 |  | - | 2 | - | - | 22 | - | - |  | - | - | -
Average | - | 3.699 | 5.3484 | 1.7581 | 0.000 | 3319.3548 | 5775.8065 | - | 53.5177 | 0.050645 | - |  | - | - | - | 6.8729 | 6.8506 | 6.6384 | 12.371 | 12.3581 | 13.2194 |  | 4.4839 | 0.13677 | 0.1 | Average | 180.5 | 5290.7632 | 124.2 | 3624.941 | 12.3571 | 382.0715 | 8.8571 | 192.0714 | 5643.2473 | 84.8 | 2465.8828 | 20.9286 | 642.1586 |  | 35027.3846 | 3.6923 | 2.4808 | 19.0769 | 26.4615 | 15.7692 |  |  | 15.7692 | - | -
[13 empty] | Geometric Mean : |  | 8.5843 | [14 empty] | Percent Removal : |  | 92.7785 |  |  |  | Percent Removal : |  | 89.1038

## Graph May08
Plant Capacity
3.85 mgd

## June 08
BRUNSWICK SEWER DISTRICT | [11 empty] | State Discharge License Number W 002600-5L-C-R | [9 empty] | Certifying Official: |  |  | Francis E. McVey | BRUNSWICK SEWER DISTRICT | [13 empty] | State Discharge License Number W 002600-5L-C-R | [11 empty] | BRUNSWICK SEWER DISTRICT | [9 empty] | State Discharge License Number W 002600-5L-C-R
Monthly Report of Treatment Operations : |  |  |  |  | June | 2008 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [12 empty] | General Manager | Monthly Report of Treatment Operations : |  |  |  |  | June | 2008 | [7 empty] | N.P.D.E.S. Permit Number ME 0100102 | [9 empty] | Page 2. |  | Monthly Report of Treatment Operations : |  |  | June | 2008 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [7 empty] | Page 3.
SETTLEABLE
| FLOW | [6 empty] | WEATHER |  |  |  |  | DISINFECTION |  |  | P.H. |  |  | TEMPERATURE |  |  |  | SOLIDS |  |  |  | BIOCHEMICAL OXYGEN DEMAND | [6 empty] | TOTAL SUSPENDED SOLIDS | [6 empty] | SLUDGE DEWATERING | [7 empty] | SLUDGE UTILIZATION |  |  |  | SUMMARY DATA | [11 empty] | HIGH WEEKLY AVERAGE VALUES
|  | Total | Maxim. | Minim. | [8 empty] | Hypo - | [37 empty] | Stored |  |  |  | LOADING |  |  | CONCENTRATION |  |  |  | REPORTING |  |  |  | BOD |  | TSS |  |  | SETTLEABLE SOLIDS
| Totalizer | Flow | Flow | Flow | Flow | Holding | Septic |  | Average | Total | Grit |  | chlorite | Chlorine | [18 empty] | CBOD | [7 empty] | Quantity | Feed | Filter |  | Cake | Sludge | Lime | Average | Quantity |  | or |  |  |  | Monthly | Daily |  | Mo Aver | High Wkly | Daily |  |  |  | Sample
Date | Reading | Treated | (instant.) | (instant.) | By-passed | Received | Added | Conditions | Temp. | Precip. | Removed |  | Used | Residual | E. Coli | Influent | Primary | Effluent | Influent | Primary | Effluent |  | Influent | Primary | Effluent | Date | Influent | Influent | Primary | Primary | Effluent | Effluent | Effluent | Influent | Influent | Primary | Primary | Effluent | Effluent |  | Dewatered | Solids | Operation | Polymer | Dry Solid | Dewatered | Added | pH | Utilized | Site | Spread |  |  |  | Average | Maximum | Units | Minimum | Average | Maximum | Units | Exceptions | Frequency | Type |  | High Weekly Average |  | High Weekly Average |  |  | High Weekly Average
|  | (MG) | (MG) | (MG) | (MG) | (gallons) | (gallons) |  | (deg. F.) | (inches) | (cu. yd.) |  | (gallons) | (mg/L) | (#/100) | (s.u.) | (s.u.) | (s.u.) | (deg. C.) | (deg. C.) | (deg. C.) |  | (ml/L) | (ml/L) | (ml/L) |  | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) |  | (gallons) | (%) | (hours) | (lbs) | (%) | (cu. yd.) | (lbs) | (s.u.) | (cu. yd.) | [16 empty] | (mg / L) | (lbs / day) | (mg / L) | (lbs / day) |  | (mg / L)
7191257
1 | 7194220 | 2.963 | 4.1 | 1 | 0.00 | 0 | 0 | CLOUDY | 63.3 | 0.01 |  |  | 30.5 | 0.39 |  | 6.73 | 6.77 | 6.17 | 13.1 | 13.5 | 15.1 |  | 7.5 | 0.2 | 0.1 | 1 | [26 empty] | BOD, 5-day | Reporting : | 308.3798 | 386.0669 | (lbs / day) | 15.0833 | 16.6667 | 17 | (mg / L) | 0 | 03/07 | 24 | Week 1 | 16.6667 | 373.3429 | 28.6667 | 643.9258 |  | 0.1 | check formulas for designation of weeks
2 | 7196782 | 2.562 | 4.8 | 1 | 0.00 | 3700 | 9000 | CLEAR | 59.5 | 0 |  |  | 25.4 | 0.44 | 2 | 6.99 | 6.9 | 6.23 | 13.7 | 13.6 | 15.2 |  | 4 | <0.1 | <0.1 | 2 | [14 empty] | 45114 | 4 | 3.25 | 27.9 | 22 | 26 |  |  | 26 | Hawk Ridge | COMPOST |  | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24
3 | 7199424 | 2.642 | 4.4 | 1 | 0.00 | 1300 | 10000 | CLEAR | 62.1 | 0.03 |  |  | 28.7 | 0.5 | 3 | 6.9 | 6.93 | 6.34 | 14.1 | 14.2 | 15.6 |  | 8 | 0.2 | <0.1 | 3 | [14 empty] | 39718 | 3 | 3.25 | 21.7 | 22 | 26 |  |  | 26 | Hawk Ridge | COMPOST | [13 empty] | Week 2 | 15 | 310.4343 | 21.6667 | 448.2083 |  | 0.1 | identifies cell for keyed data entry
4 | 7201957 | 2.533 | 4.8 | 1 | 0.00 | 4300 | 9250 | CLOUDY | 58.2 | 0.22 |  |  | 27.9 | 0.43 | 1 | 6.87 | 7.05 | 6.43 | 14.1 | 13.9 | 15.6 |  | 5 | <0.1 | <0.1 | 4 | 241 | 5091.178 |  |  | 17 | 359.1287 | 13 | 228 | 4816.5502 |  |  | 27 | 570.3809
5 | 7204766 | 2.809 | 5.6 | 1 | 0.00 | 9000 | 12500 | CLOUDY | 57.7 | 0.04 |  |  | 31.9 | 0.47 |  | 6.83 | 6.76 | 6.33 | 14.3 | 15 | 15.2 |  | 4.5 | 0.5 | <0.1 | 5 | 238 | 5575.6403 |  |  | 16 | 374.833 | 11 | 330 | 7730.9298 |  |  | 30 | 702.8118 |  | 41812 | 4 | 3.5 | 24.8 | 22 | 27 |  |  | 27 | Hawk Ridge | COMPOST | [13 empty] | Week 3 | 15 | 289.5231 | 20 | 386.0225 |  | 0.1
6 | 7207489 | 2.723 | 4.3 | 1.2 | 0.00 | 8000 | 13750 | CLOUDY | 53.2 | 0.1 |  |  | 28.9 | 0.49 |  | 6.98 | 6.99 | 6.37 | 14.1 | 14.1 | 15.5 |  | 6.5 | <0.1 | <0.1 | 6 | 201 | 4564.6738 | 140 | 3179.3748 | 17 | 386.0669 | 13 | 244 | 5541.1961 | 114 | 2588.9195 | 29 | 658.5848 | [13 empty] | pH | Reporting : | - | - | - | 6.03 | - | 6.62 | (s.u.) | 0 | 01/01 | GR
7 | 7210049 | 2.56 | 4.1 | 1 | 0.00 | 0 | 0 | CLOUDY | 58.6 | 0.01 |  |  | 25.1 | 0.41 |  | 6.85 | 6.84 | 6.29 | 14 | 13.8 | 15 |  | 2.5 | <0.1 | <0.1 | 7 | [26 empty] | Effluent | Permit : | - | - | - | 6 | - | 8.5 | (s.u.) | - | 01/01 | GR | Week 4 | 13.6667 | 260.2191 | 19 | 362.8901 |  | 0.1
8 | 7212488 | 2.439 | 4.4 | 1 | 0.00 | 0 | 0 | CLEAR | 69.8 | 0 |  |  | 27.8 | 0.4 |  | 6.9 | 7.11 | 6.4 | 13.3 | 13.9 | 15.6 |  | 5 | <0.1 | <0.1 | 8
9 | 7215039 | 2.551 | 4.8 | 1 | 0.00 | 1100 | 7750 | CLEAR | 73.5 | 0 |  |  | 27.8 | 0.58 | 1 | 6.93 | 6.05 | 6.37 | 15.2 | 16.3 | 16.8 |  | 17 | 1.5 | <0.1 | 9 | [14 empty] | 46213 | 5 | 3 | 27.9 | 26 | 28 |  |  | 28 | Hawk Ridge | COMPOST | [13 empty] | Week 5
10 | 7217611 | 2.572 | 4 | 0.9 | 0.00 | 1000 | 9800 | CLOUDY | 65.6 | 0.06 |  |  | 30.7 | 0.44 | 13.2 | 7.06 | 7.25 | 6.61 | 14.8 | 14.9 | 16.8 |  | 9.5 | 0.1 | <0.1 | 10 | [14 empty] | 45205 | 4 | 3 | 24.8 | 28 | 26 |  |  | 26 | Hawk Ridge | COMPOST
11 | 7220025 | 2.414 | 4 | 0.9 | 0.00 | 3500 | 12750 | CLEAR | 68.7 | 0.11 |  |  | 29.5 | 0.4 | 2 | 6.93 | 7.05 | 6.46 | 14.1 | 14.3 | 16.2 |  | 9.5 | <0.1 | <0.1 | 11 | 202 | 4066.8175 |  |  | 16 | 322.1242 | 11 | 280 | 5637.1728 |  |  | 20 | 402.6552 | [13 empty] | TSS | Reporting : | 460.2617 | 702.8118 | (lbs / day) | 22.3333 | 28.6667 | 30 | (mg / L) | 0 | 03/07 | 24
12 | 7222424 | 2.399 | 4.6 | 0.8 | 0.00 | 3700 | 9500 | CLEAR | 66 | 0 |  |  | 26.1 | 0.47 |  | 7.14 | 7.03 | 6.06 | 15.1 | 15.7 | 16.4 |  | 9.5 | 0.1 | <0.1 | 12 | 255 | 5101.9533 |  |  | 13 | 260.0996 | 9 | 290 | 5802.2214 |  |  | 22 | 440.1685 |  | 26623 | 5 | 1.75 | 15.5 | 27 | 13 |  |  | 13 | Hawk Ridge | COMPOST |  | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24 | Maximum | 16.6667 | 373.3429 | 28.6667 | 643.9258 |  | 0.1
13 | 7225040 | 2.616 | 4 | 0.8 | 0.00 | 6500 | 9500 | CLEAR | 64.1 | 0 |  |  | 29 | 0.28 |  | 7.09 | 7.14 | 6.03 | 14.9 | 14.5 | 15.7 |  | 8.5 | <0.1 | <0.1 | 13 | 217 | 4734.3845 | 145 | 3163.5288 | 16 | 349.079 | 11 | 326 | 7112.4854 | 100 | 2181.744 | 23 | 501.8011
14 | 7227348 | 2.308 | 4.2 | 0.8 | 0.00 | 1500 | 3000 | CLEAR | 62.2 | 0 |  |  | 26 | 0.49 |  | 6.92 | 7.13 | 6.05 | 13.6 | 14.1 | 15.4 |  | 5 | <0.1 | <0.1 | 14
15 | 7229633 | 2.285 | 4 | 0.8 | 0.00 | 1000 | 2000 | RAIN | 57.2 | 0.23 |  |  | 19.8 | 0.52 |  | 7.15 | 7.21 | 6.06 | 14.1 | 14.3 | 15.8 |  | 6 | <0.1 | <0.1 | 15
16 | 7231933 | 2.3 | 4.1 | 0.9 | 0.00 | 3000 | 8250 | CLOUDY | 58.1 | 0.03 |  |  | 23 | 0.45 | 1 | 6.92 | 7.05 | 6.09 | 14.9 | 14.3 | 15.8 |  | 3.5 | <0.1 | <0.1 | 16 | [14 empty] | 57784 | 3 | 4 | 24.8 | 31 | 24 | 1920 | 12.36 | 24 | EGYPT | STORE |  | SETTLEABLE
17 | 7234321 | 2.388 | 4 | 0.8 | 0.00 | 2700 | 10500 | LT RAIN | 60.8 | 0.13 |  |  | 24 | 0.49 | 4.1 | 7.05 | 7.23 | 6.44 | 15.2 | 15.1 | 16.1 |  | 8.5 | <0.1 | <0.1 | 17 | [26 empty] | SOLIDS | Reporting : | - | - | - | - | - | 0.1 | (mg / L) | 0 | 01/01 | GR
18 | 7236638 | 2.317 | 3.8 | 0.8 | 0.00 | 5800 | 9000 | CLOUDY | 61 | 0 |  |  | 24.6 | 0.47 | 3.1 | 7.19 | 7.04 | 6.2 | 15.1 | 15 | 16.1 |  | 6.5 | <0.1 | <0.1 | 18 | 291 | 5623.22 |  |  | 15 | 289.8567 | 11 | 257 | 4966.2115 |  |  | 19 | 367.1518 | [13 empty] | Effluent | Permit : | - | - | - | - | (Report) | 0.3 | (mg / L) | - | 01/01 | GR
19 | 7238950 | 2.312 | 4.3 | 0.8 | 0.00 | 6000 | 9500 | CLOUDY | 612 | 0 |  |  | 24.8 | 0.48 |  | 6.84 | 7.21 | 6.23 | 15.1 | 15.1 | 16.4 |  | 6.5 | 0.1 | <0.1 | 19 | 242 | 4666.2634 |  |  | 15 | 289.2312 | 11 | 258 | 4974.7766 |  |  | 20 | 385.6416 |  | 75977 | 4 | 4.75 | 37.2 | 31 | 36 | 2280 | 12.34 | 36 | EGYPT | STORE
20 | 7241264 | 2.314 | 4.1 | 0.8 | 0.00 | 5900 | 11500 | CLOUDY | 61.7 | 0.03 |  |  | 23.3 | 0.42 |  | 6.6 | 7.02 | 6.22 | 15.3 | 15.1 | 16.2 |  | 6 | <0.1 | <0.1 | 20 | 311 | 6001.9144 | 181 | 3493.0756 | 15 | 289.4814 | 10 | 352 | 6793.1635 | 114 | 2200.0586 | 21 | 405.274
21 | 7243625 | 2.361 | 3.9 | 0.8 | 0.00 | 15300 | 8000 | CLOUDY | 63.3 | 0.01 |  |  | 25.4 | 0.43 |  | 7.08 | 7.38 | 6.31 | 14.2 | 15.2 | 16.7 |  | 3 | <0.1 | <0.1 | 21
22 | 7245826 | 2.201 | 3.8 | 0.8 | 0.00 | 0 | 2000 | CLOUDY | 63.9 | 0.19 |  |  | 24.5 | 0.54 |  | 6.7 | 7.2 | 6.23 | 14.2 | 14.8 | 16.7 |  | 4 | <0.1 | <0.1 | 22 | [26 empty] | FLOW | Reporting : | 2.4175 | 2.963 | (MGD) | - | - | - | - | 0 | 99/99 | RC |  |  |  | CBOD
23 | 7248011 | 2.185 | 3.8 | 0.8 | 0.00 | 2000 | 8000 | CLOUDY | 65.4 | 0.06 |  |  | 25.1 | 0.5 | 1 | 7.1 | 7.35 | 6.55 | 14.9 | 15 | 16.6 |  | 8 | <0.1 | <0.1 | 23 | [14 empty] | 55867 | 4 | 3.5 | 27.9 | 34 | 24 | 1785 | 12.35 | 24 | EGYPT | STORE |  | Effluent | Permit : | 3.85 | (Report) | (MGD) | - | - | - | - | - | 99/99 | RC
24 | 7250255 | 2.244 | 3.8 | 0.8 | 0.00 | 2300 | 11000 | CLEAR | 66.8 | 0.05 |  |  | 29.7 | 0.45 | 1 | 6.98 | 7.35 | 6.62 | 15.2 | 15 | 16.6 |  | 7.5 | <0.1 | <0.1 | 24 | [41 empty] | % Removal
25 | 7252502 | 2.247 | 4 | 0.8 | 0.00 | 3500 | 12250 | CLEAR | 68 | 0.01 |  |  | 25.2 | 0.46 | 2 | 7.16 | 7.3 | 6.39 | 15.7 | 15.5 | 16.7 |  | 9 | <0.1 | <0.1 | 25 | 304 | 5696.9539 |  |  | 14 | 262.3597 | 10 | 272 | 5097.2746 |  |  | 17 | 318.5797
26 | 7254742 | 2.24 | 4.4 | 0.7 | 0.00 | 1200 | 9250 | CLEAR | 68.8 | 0 |  |  | 24 | 0.5 |  | 7.22 | 7.36 | 6.34 | 15.1 | 15.3 | 17 |  | 6 | <0.1 | <0.1 | 26 | 279 | 5212.1664 |  |  | 13 | 242.8608 | 8 | 276 | 5156.1216 |  |  | 17 | 317.5872 |  | 47456 | 4 | 3.5 | 27.9 | 31 | 24 | 1680 | 12.41 | 24 | EGYPT | STORE | [16 empty] | 95.8141
27 | 7257101 | 2.359 | 3.9 | 0.7 | 0.00 | 1300 | 14000 | CLEAR | 70.4 | 0 |  |  | 28.8 | 0.41 |  | 7.26 | 7.46 | 6.32 | 15.8 | 15.9 | 17.6 |  | 12 | <0.1 | <0.1 | 27 | 248 | 4879.1669 | 157 | 3088.8274 | 14 | 275.4368 | 9 | 278 | 5469.3887 | 82 | 1613.2729 | 23 | 452.5034 | [13 empty] | BOD, 5-day | Reporting : | - | - | - | 93.9548 | - | - | (percent) | 0 | 01/30 | CA
28 | 7259290 | 2.189 | 3.8 | 0.7 | 0.00 | 2000 | 2000 | CLOUDY | 60.6 | 0.02 |  |  | 25.8 | 0.49 |  | 6.92 | 7.15 | 6.6 | 16.4 | 16.2 | 17.6 |  | 7 | <0.1 | <0.1 | 28 | [26 empty] | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
29 | 7261372 | 2.082 | 7 | 0.8 | 0.00 | 0 | 0 | CLOUDY | 62.5 | 1.05 |  |  | 24.3 | 0.61 |  | 7.02 | 7.18 | 6.55 | 16.1 | 15.7 | 16.9 |  | 6 | <0.1 | <0.1 | 29
30 | 7263781 | 2.409 | 4.4 | 0.7 | 0.00 | 500 | 5000 | CLOUDY | 69.2 | 0.01 |  |  | 25.9 | 0.49 | 3.1 | 7.1 | 7.24 | 6.62 | 16.1 | 16.1 | 17.9 |  | 7.5 | 0.5 | <0.1 | 30 | [14 empty] | 54994 | 3 | 3.5 | 24.8 | 32 | 24 | 1785 | 12.28 | 24 | EGYPT | STORE
31 | [25 empty] | 31
[53 empty] | TSS | Reporting : | - | - | - | 92.0967 | - | - | (percent) | 0 | 01/30 | CA
Total | 72524 | 72.524 | - | - | 0 | 96100 | 229050 | - | - | 2.4 | 0.0 |  | 793.5 | - | - | - | - | - | - | - | - |  | - | - | - | Total | - | - | - | - | - | - | - | - | - | - | - | - | - |  | 536763 | - | 37 | 285.2 | - | 278 | 9450 | - | 278 | - | - |  | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
Maximum | - | 2.963 | 7 | 1.2 | 0 | 15300 | 14000 | - | 612 | 1.05 | - |  | - | 0.61 | 13.2 | 7.26 | 7.46 | 6.62 | 16.4 | 16.3 | 17.9 |  | 17 | 1.5 | 0.1 | Maximum | 311 | 6001.9144 | 181 | 3493.0756 | 17 | 386.0669 | 13 | 352 | 7730.9298 | 114 | 2588.9195 | 30 | 702.8118 |  | - | 5 | - | - | 34 | - | - | 12.41 | - | - | -
Minimum | - | 2.082 | 3.8 | 0.7 | 0 | 0 | 0 | - | 53.2 | 0 | - |  | - | 0.28 | 1 | 6.6 | 6.05 | 6.03 | 13.1 | 13.5 | 15 |  | 2.5 | 0.1 | 0.1 | Minimum | 201 | 4066.8175 | 140 | 3088.8274 | 13 | 242.8608 | 8 | 228 | 4816.5502 | 82 | 1613.2729 | 17 | 317.5872 |  | - | 3 | - | - | 22 | - | - | 12.28 | - | - | -
Average | - | 2.4175 | 4.3067 | 0.86333 | 0.000 | 3203.3333 | 7635 | - | 81.74 | 0.08 | - |  | - | - | - | 6.9803 | 7.091 | 6.3303 | 14.7267 | 14.8467 | 16.2267 |  | 6.9667 | 0.4 | 0.1 | Average | 252.4167 | 5101.1944 | 155.75 | 3231.2016 | 15.0833 | 308.3798 | 10.5833 | 282.5833 | 5758.1243 | 102.5 | 2145.9988 | 22.3333 | 460.2617 |  | 48796.6364 | 3.9091 | 3.3636 | 25.9273 | 27.8182 | 25.2727 | 1890 | 12.348 | 25.2727 | - | -
[13 empty] | Geometric Mean : |  | 2.0659 | [14 empty] | Percent Removal : |  | 93.9548 |  |  |  | Percent Removal : |  | 92.0967

## Graph Jun08
Plant Capacity
3.85 mgd

## July 08
BRUNSWICK SEWER DISTRICT | [11 empty] | State Discharge License Number W 002600-5L-C-R | [9 empty] | Certifying Official: |  |  | Francis E. McVey | BRUNSWICK SEWER DISTRICT | [13 empty] | State Discharge License Number W 002600-5L-C-R | [11 empty] | BRUNSWICK SEWER DISTRICT | [9 empty] | State Discharge License Number W 002600-5L-C-R
Monthly Report of Treatment Operations : |  |  |  |  | July | 2008 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [12 empty] | General Manager | Monthly Report of Treatment Operations : |  |  |  |  | July | 2008 | [7 empty] | N.P.D.E.S. Permit Number ME 0100102 | [9 empty] | Page 2. |  | Monthly Report of Treatment Operations : |  |  | July | 2008 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [7 empty] | Page 3.
SETTLEABLE
| FLOW | [6 empty] | WEATHER |  |  |  |  | DISINFECTION |  |  | P.H. |  |  | TEMPERATURE |  |  |  | SOLIDS |  |  |  | BIOCHEMICAL OXYGEN DEMAND | [6 empty] | TOTAL SUSPENDED SOLIDS | [6 empty] | SLUDGE DEWATERING | [7 empty] | SLUDGE UTILIZATION |  |  |  | SUMMARY DATA | [11 empty] | HIGH WEEKLY AVERAGE VALUES
|  | Total | Maxim. | Minim. | [8 empty] | Hypo - | [37 empty] | Stored |  |  |  | LOADING |  |  | CONCENTRATION |  |  |  | REPORTING |  |  |  | BOD |  | TSS |  |  | SETTLEABLE SOLIDS
| Totalizer | Flow | Flow | Flow | Flow | Holding | Septic |  | Average | Total | Grit |  | chlorite | Chlorine | [18 empty] | CBOD | [7 empty] | Quantity | Feed | Filter |  | Cake | Sludge | Lime | Average | Quantity |  | or |  |  |  | Monthly | Daily |  | Mo Aver | High Wkly | Daily |  |  |  | Sample
Date | Reading | Treated | (instant.) | (instant.) | By-passed | Received | Added | Conditions | Temp. | Precip. | Removed |  | Used | Residual | E. Coli | Influent | Primary | Effluent | Influent | Primary | Effluent |  | Influent | Primary | Effluent | Date | Influent | Influent | Primary | Primary | Effluent | Effluent | Effluent | Influent | Influent | Primary | Primary | Effluent | Effluent |  | Dewatered | Solids | Operation | Polymer | Dry Solid | Dewatered | Added | pH | Utilized | Site | Spread |  |  |  | Average | Maximum | Units | Minimum | Average | Maximum | Units | Exceptions | Frequency | Type |  | High Weekly Average |  | High Weekly Average |  |  | High Weekly Average
|  | (MG) | (MG) | (MG) | (MG) | (gallons) | (gallons) |  | (deg. F.) | (inches) | (cu. yd.) |  | (gallons) | (mg/L) | (#/100) | (s.u.) | (s.u.) | (s.u.) | (deg. C.) | (deg. C.) | (deg. C.) |  | (ml/L) | (ml/L) | (ml/L) |  | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) |  | (gallons) | (%) | (hours) | (lbs) | (%) | (cu. yd.) | (lbs) | (s.u.) | (cu. yd.) | [16 empty] | (mg / L) | (lbs / day) | (mg / L) | (lbs / day) |  | (mg / L)
7263781
1 | 7266142 | 2.361 | 4 | 0.7 | 0.00 | 4700 | 4000 | CLEAR | 68.5 | 0.01 |  |  | 30.1 | 0.42 | 38.8 | 6.96 | 7.29 | 6.74 | 16.6 | 16 | 18.1 |  | 4 | <0.1 | 0.1 | 1 | 289 | 5690.6239 |  |  | 10 | 196.9074 | 8 | 266 | 5237.7368 |  |  | 19 | 374.1241 | [13 empty] | BOD, 5-day | Reporting : | 194.0337 | 272.8848 | (lbs / day) | 11 | 11.6667 | 16 | (mg / L) | 0 | 03/07 | 24 | Week 1 | 10.3333 | 194.486 | 15.3333 | 290.346 |  | 0.1 | check formulas for designation of weeks
2 | 7268381 | 2.239 | 4 | 0.7 | 0.00 | 2000 | 6500 | CLEAR | 69.3 | 0.01 |  |  | 29.6 | 0.47 | 32.6 | 7.22 | 7.27 | 6.6 | 15.5 | 16 | 18.1 |  | 7 | <0.1 | 0.1 | 2 | 255 | 4761.6813 |  |  | 11 | 205.4059 | 8 | 220 | 4108.1172 |  |  | 14 | 261.4256 | [13 empty] | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24
3 | 7270553 | 2.172 | 3.9 | 0.6 | 0.00 | 1700 | 6250 | CLEAR | 70.4 | 0 |  |  | 31.5 | 0.49 |  | 7.19 | 6.66 | 6.33 | 16.1 | 16.4 | 17.6 |  | 5 | <0.1 | 0.1 | 3 | 258 | 4673.5358 | 129 | 2336.7679 | 10 | 181.1448 | 7 | 206 | 3731.5829 | 80 | 1449.1584 | 13 | 235.4882 |  | 68045 | 3 | 4.5 | 40.3 | 31 | 36 | 2160 | 12.35 | 36 | EGYPT | STORE | [13 empty] | Week 2 | 10.3333 | 185.6595 | 13.3333 | 237.3119 |  | 0.1 | identifies cell for keyed data entry
4 | 7272692 | 2.139 | 3.8 | 0.6 | 0.00 | 0 | 0 | CLEAR | 65.8 | 0 |  |  | 21.6 | 0.54 |  | 6.94 | 7.23 | 7 | 14.7 | 15.7 | 17.3 |  | 5.5 | <0.1 | 0.1 | 4
5 | 7274606 | 1.914 | 3.8 | 0.6 | 0.00 | 0 | 0 | CLEAR | 65.9 | 0 |  |  | 18.2 | 0.45 |  | 7.18 | 7.31 | 6.69 | 15.8 | 15.7 | 16.8 |  | 10 | 0.2 | 0.1 | 5 | [38 empty] | Week 3 | 9.6667 | 160.9759 | 14.3333 | 238.9493 |  | 0.1
6 | 7276561 | 1.955 | 3.8 | 0.7 | 0.00 | 0 | 0 | CLOUDY | 67.1 | 0 |  |  | 21.7 | 0.47 |  | 6.79 | 7.25 | 6.57 | 16.5 | 15.8 | 17.1 |  | 2 | <0.1 | 0.1 | 6 | [26 empty] | pH | Reporting : | - | - | - | 6.33 | - | 7.12 | (s.u.) | 0 | 01/01 | GR
7 | 7278591 | 2.03 | 3.8 | 0.7 | 0.00 | 5600 | 9300 | CLEAR | 72.3 | 0 |  |  | 19 | 0.41 | 5.2 | 7.18 | 7.22 | 6.7 | 15.9 | 16.2 | 17.8 |  | 7 | <0.1 | 0.1 | 7 | [14 empty] | 72692 | 2 | 4 | 31 | 31 | 24 | 1800 | 12.37 | 24 | EGYPT | STORE |  | Effluent | Permit : | - | - | - | 6 | - | 8.5 | (s.u.) | - | 01/01 | GR | Week 4 | 11.6667 | 207.1545 | 17.6667 | 313.9287 |  | 0.1
8 | 7280725 | 2.134 | 3.7 | 0.6 | 0.00 | 3500 | 6000 | CLEAR | 74.8 | 0 |  |  | 20.7 | 0.47 | 27.5 | 7.3 | 7.35 | 6.87 | 16.7 | 16.6 | 18.5 |  | 10 | 0.1 | 0.1 | 8
9 | 7282849 | 2.124 | 5 | 0.6 | 0.00 | 10700 | 9000 | CLEAR | 73.4 | 0.06 |  |  | 19.8 | 0.48 | 5.2 | 7.34 | 7.39 | 6.88 | 16.5 | 16.9 | 18.7 |  | 7 | <0.1 | 0.1 | 9 | 263 | 4658.8241 |  |  | 13 | 230.2841 | 10 | 324 | 5739.3878 |  |  | 17 | 301.1407 | [25 empty] | Week 5
10 | 7285119 | 2.27 | 3.6 | 0.6 | 0.00 | 2000 | 8250 | CLOUDY | 74.4 | 0.01 |  |  | 23.1 | 0.45 |  | 7.19 | 7.39 | 6.81 | 17.2 | 16.9 | 18.6 |  | 8 | <0.1 | 0.1 | 10 | 273 | 5168.3814 |  |  | 10 | 189.318 | 7 | 218 | 4127.1324 |  |  | 9 | 170.3862 |  | 55070 | 3 | 3.5 | 24.8 | 31 | 20 | 1680 | 12.33 | 20 | EGYPT | STORE
11 | 7287178 | 2.059 | 3.6 | 0.6 | 0.00 | 200 | 12750 | CLEAR | 67 | 0 | 6 |  | 19.5 | 0.52 |  | 7.27 | 7.34 | 6.92 | 15.8 | 16.5 | 17.9 |  | 8.5 | 0.1 | 0.1 | 11 | 222 | 3812.1973 | 135 | 2318.2281 | 8 | 137.3765 | 7 | 216 | 3709.165 | 71 | 1219.2163 | 14 | 240.4088 | [13 empty] | TSS | Reporting : | 271.218 | 374.1241 | (lbs / day) | 15.3571 | 17.6667 | 19 | (mg / L) | 0 | 03/07 | 24
12 | 7289214 | 2.036 | 3.6 | 0.6 | 0.00 | 2500 | 3000 | CLEAR | 68.5 | 0 |  |  | 19.5 | 0.45 |  | 7.17 | 7.36 | 6.61 | 15.9 | 16.6 | 17.9 |  | 9 | 0.1 | 0.1 | 12 | [26 empty] | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24 | Maximum | 11.6667 | 207.1545 | 17.6667 | 313.9287 |  | 0.1
13 | 7291157 | 1.943 | 3.5 | 0.6 | 0.00 | 0 | 0 | CLOUDY | 69.2 | 0 |  |  | 19.4 | 0.49 |  | 7.13 | 7.56 | 6.76 | 15.6 | 16.5 | 18.3 |  | 4.5 | 0.1 | 0.1 | 13
14 | 7293104 | 1.947 | 3.7 | 0.6 | 0.00 | 5100 | 6500 | CLOUDY | 70.5 | 0.03 |  |  | 17.5 | 0.53 | 2 | 7.41 | 7.45 | 6.91 | 16.8 | 16.8 | 18.7 |  | 7.5 | 0.1 | 0.1 | 14
15 | 7295158 | 2.054 | 3.7 | 0.6 | 0.00 | 0 | 6500 | CLEAR | 71.9 | 0 |  |  | 18.7 | 0.47 | 5.1 | 7.34 | 6.52 | 6.67 | 17 | 17.6 | 18.6 |  | 11 | 0.4 | 0.1 | 15 | [14 empty] | 63844 | 3 | 3.5 | 31 | 31 | 24 | 1680 | 12.39 | 24 | EGYPT | STORE
16 | 7297182 | 2.024 | 3.6 | 0.6 | 0.00 | 2300 | 9000 | CLEAR | 72.2 | 0 |  |  | 17.1 | 0.47 | 1 | 7.2 | 7.43 | 7 | 16.4 | 16.8 | 18.3 |  | 8 | 0.1 | 0.1 | 16 | 290 | 4895.2464 |  |  | 10 | 168.8016 | 7 | 254 | 4287.5606 |  |  | 17 | 286.9627 | [13 empty] | SETTLEABLE
17 | 7299167 | 1.985 | 3.6 | 0.6 | 0.00 | 1900 | 11750 | CLEAR | 74 | 0 |  |  | 16 | 0.42 |  | 7.45 | 7.39 | 6.78 | 17 | 17.9 | 18.8 |  | 12 | 0.2 | 0.1 | 17 | 277 | 4585.7073 |  |  | 9 | 148.9941 | 6 | 286 | 4734.7014 |  |  | 13 | 215.2137 |  | 48231 | 3 | 3 | 21.7 | 31 | 20 | 1530 | 12.3 | 20 | EGYPT | STORE |  | SOLIDS | Reporting : | - | - | - | - | 0.1 | 0.1 | (mg / L) | 0 | 01/01 | GR
18 | 7301147 | 1.98 | 4.4 | 0.5 | 0.00 | 2200 | 10750 | CLEAR | 69.4 | 0.01 |  |  | 18.8 | 0.48 |  | 7.27 | 7.29 | 6.92 | 17.1 | 17.9 | 19.1 |  | 10 | 0.1 | 0.1 | 18 | 307 | 5069.5524 | 165 | 2724.678 | 10 | 165.132 | 8 | 340 | 5614.488 | 84 | 1387.1088 | 13 | 214.6716 | [13 empty] | Effluent | Permit : | - | - | - | - | (Report) | 0.3 | (mg / L) | - | 01/01 | GR
19 | 7303219 | 2.072 | 3.6 | 0.6 | 0.00 | 0 | 4000 | LT RAIN | 72.8 | 0 |  |  | 17.8 | 0.44 |  | 7.12 | 7.35 | 6.7 | 16 | 17.2 | 18.9 |  | 5 | 0.1 | 0.1 | 19
20 | 7305143 | 1.924 | 3.6 | 0.5 | 0.00 | 0 | 0 | CLEAR | 69.6 | 0.03 |  |  | 17.2 | 0.44 |  | 7.21 | 7.42 | 6.85 | 16.4 | 17.5 | 19.2 |  | 4 | 0.1 | 0.1 | 20
21 | 7307111 | 1.968 | 4.4 | 0.5 | 0.00 | 6400 | 6000 | CLOUDY | 69.3 | 0.04 |  |  | 21.3 | 0.53 |  | 7.21 | 7.35 | 6.84 | 17.2 | 17.5 | 18.9 |  | 7 | 0.1 | 0.1 | 21 | [14 empty] | 60753 | 3 | 3.75 | 31 | 33 | 24 | 1912.5 | 12.43 | 24 | EGYPT | STORE
22 | 7309170 | 2.059 | 3.6 | 0.6 | 0.00 | 2750 | 9300 | CLEAR | 69 | 0 |  |  | 18.7 | 0.52 | 5.2 | 7.25 | 7.45 | 7.04 | 17 | 17.4 | 19 |  | 7 | 0.1 | 0.1 | 22 | [26 empty] | FLOW | Reporting : | 2.0576 | 2.361 | (MGD) | - | - | - | - | 0 | 99/99 | RC |  |  |  | CBOD
23 | 7311206 | 2.036 | 3.5 | 0.8 | 0.00 | 3300 | 9500 | CLOUDY | 66 | 0.03 |  |  | 17 | 0.43 | 1 | 7.24 | 7.31 | 6.75 | 16.9 | 17.6 | 19.1 |  | 10 | 0.1 | 0.1 | 23 | 331 | 5620.4594 |  |  | 11 | 186.7826 | 8 | 276 | 4686.5462 |  |  | 15 | 254.7036 | [13 empty] | Effluent | Permit : | 3.85 | (Report) | (MGD) | - | - | - | - | - | 99/99 | RC
24 | 7313352 | 2.146 | 3.8 | 0.7 | 0.00 | 7200 | 9000 | RAIN | 69.8 | 0.05 |  |  | 20.1 | 0.4 | 3.1 | 7.29 | 7.6 | 6.57 | 17.6 | 17.7 | 19.2 |  | 7 | 0.1 | 0.1 | 24 | 275 | 4921.851 |  |  | 10 | 178.9764 | 7 | 254 | 4546.0006 |  |  | 19 | 340.0552 |  | 63690 | 4 | 3.5 | 31 | 32 | 24 | 1785 | 12.34 | 24 | EGYPT | STORE | [16 empty] | % Removal
25 | 7315542 | 2.19 | 3.8 | 0.6 | 0.00 | 1500 | 10500 | CLOUDY | 69.4 | 0 |  |  | 20.9 | 0.59 |  | 7.25 | 7.41 | 6.98 | 17.3 | 17.7 | 19.2 |  | 8 | 0.1 | 0.1 | 25 | 267 | 4876.6482 | 170 | 3104.982 | 14 | 255.7044 | 9 | 278 | 5077.5588 | 79 | 1442.9034 | 19 | 347.0274
26 | 7317581 | 2.039 | 4.2 | 0.5 | 0.00 | 3500 | 6000 | CLOUDY | 71 | 0 |  |  | 22 | 0.44 |  | 7.06 | 7.43 | 6.86 | 17.7 | 18 | 19.5 |  | 10 | 0.1 | 0.1 | 26 | [41 empty] | 97.215
27 | 7319547 | 1.966 | 3.6 | 0.6 | 0.00 | 0 | 3500 | CLOUDY | 70.3 | 0.01 |  |  | 27.2 | 0.4 |  | 7.02 | 7.37 | 6.97 | 16.3 | 17.6 | 19.4 |  | 4 | 0.1 | 0.1 | 27 | [26 empty] | BOD, 5-day | Reporting : | - | - | - | 96.0665 | - | - | (percent) | 0 | 01/30 | CA
28 | 7321497 | 1.95 | 3.9 | 0.5 | 0.00 | 2600 | 14850 | CLEAR | 69.8 | 0 |  |  | 30 | 0.43 | 4.1 | 7.39 | 8.2 | 7.08 | 17.5 | 17.6 | 18.9 |  | 12 | 0.3 | 0.1 | 28 | [14 empty] | 49818 | 4 | 3.25 | 24.8 | 35 | 24 | 1785 | 12.27 | 24 | EGYPT | STORE |  | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
29 | 7323536 | 2.039 | 3.6 | 0.6 | 0.00 | 3300 | 5500 | CLEAR | 72.7 | 0 |  |  | 25.2 | 0.43 | 14.4 | 7.2 | 7.32 | 7.12 | 17.1 | 17.6 | 19.1 |  | 8 | 0.1 | 0.1 | 29
30 | 7325522 | 1.986 | 4.2 | 0.6 | 0.00 | 1000 | 9750 | CLEAR | 70.9 | 0 |  |  | 23.7 | 0.41 | 41 | 7.08 | 7.45 | 6.93 | 18.2 | 17.8 | 19.3 |  | 5 | 0.1 | 0.1 | 30 | 297 | 4919.2823 |  |  | 12 | 198.7589 | 9 | 326 | 5399.6162 |  |  | 15 | 248.4486
31 | 7327567 | 2.045 | 5.8 | 0.7 | 0.00 | 1500 | 9750 | CLEAR | 68.2 | 0.01 |  |  | 27.4 | 0.58 |  | 7.1 | 6.39 | 6.81 | 18.5 | 18.4 | 20 |  | 5.5 | 1.5 | 0.1 | 31 | 317 | 5406.5301 |  |  | 16 | 272.8848 | 11 | 360 | 6139.908 |  |  | 18 | 306.9954 |  | 71097 | 3 | 4.5 | 34.1 | 36 | 32 | 2295 | 12.41 | 32 | EGYPT | STORE
[53 empty] | TSS | Reporting : | - | - | - | 94.3776 | - | - | (percent) | 0 | 01/30 | CA
Total | 63786 | 63.786 | - | - | 0 | 77450 | 207200 | - | - | 0.3 | 6 |  | 670.3 | - | - | - | - | - | - | - | - |  | - | - | - | Total | - | - | - | - | - | - | - | - | - | - | - | - | - |  | 553240 | - | 33.5 | 269.7 | - | 228 | 16627.5 | - | 228 | - | - |  | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
Maximum | - | 2.361 | 5.8 | 0.8 | 0 | 10700 | 14850 | - | 74.8 | 0.06 | - |  | - | 0.59 | 41 | 7.45 | 8.2 | 7.12 | 18.5 | 18.4 | 20 |  | 12 | 1.5 | 0.1 | Maximum | 331 | 5690.6239 | 170 | 3104.982 | 16 | 272.8848 | 11 | 360 | 6139.908 | 84 | 1449.1584 | 19 | 374.1241 |  | - | 4 | - | - | 36 | - | - | 12.43 | - | - | -
Minimum | - | 1.914 | 3.5 | 0.5 | 0 | 0 | 0 | - | 65.8 | 0 | - |  | - | 0.4 | 1 | 6.79 | 6.39 | 6.33 | 14.7 | 15.7 | 16.8 |  | 2 | 0.1 | 0.1 | Minimum | 222 | 3812.1973 | 129 | 2318.2281 | 8 | 137.3765 | 6 | 206 | 3709.165 | 71 | 1219.2163 | 9 | 170.3862 |  | - | 2 | - | - | 31 | - | - | 12.27 | - | - | -
Average | - | 2.0576 | 3.8935 | 0.60968 | 0.000 | 2498.3871 | 6683.871 | - | 70.1097 | 0.0096774 | - |  | - | - | - | 7.1919 | 7.3145 | 6.8148 | 16.671 | 17.0452 | 18.5774 |  | 7.371 | 0.1913 | 0.1 | Average | 280.0714 | 4932.8944 | 149.75 | 2621.164 | 11 | 194.0337 | 8 | 273.1429 | 4795.6787 | 78.5 | 1374.5967 | 15.3571 | 271.218 |  | 61471.1111 | 3.1111 | 3.7222 | 29.9667 | 32.3333 | 25.3333 | 1847.5 | 12.3544 | 25.3333 | - | -
[13 empty] | Geometric Mean : |  | 6.7091 | [14 empty] | Percent Removal : |  | 96.0665 |  |  |  | Percent Removal : |  | 94.3776

## Graph Jul08
Plant Capacity
3.85 mgd

## August 08
BRUNSWICK SEWER DISTRICT | [11 empty] | State Discharge License Number W 002600-5L-C-R | [9 empty] | Certifying Official: |  |  | Francis E. McVey | BRUNSWICK SEWER DISTRICT | [13 empty] | State Discharge License Number W 002600-5L-C-R | [11 empty] | BRUNSWICK SEWER DISTRICT | [9 empty] | State Discharge License Number W 002600-5L-C-R
Monthly Report of Treatment Operations : |  |  |  |  | August | 2008 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [12 empty] | General Manager | Monthly Report of Treatment Operations : |  |  |  |  | August | 2008 | [7 empty] | N.P.D.E.S. Permit Number ME 0100102 | [9 empty] | Page 2. |  | Monthly Report of Treatment Operations : |  |  | August | 2008 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [7 empty] | Page 3.
SETTLEABLE
| FLOW | [6 empty] | WEATHER |  |  |  |  | DISINFECTION |  |  | P.H. |  |  | TEMPERATURE |  |  |  | SOLIDS |  |  |  | BIOCHEMICAL OXYGEN DEMAND | [6 empty] | TOTAL SUSPENDED SOLIDS | [6 empty] | SLUDGE DEWATERING | [7 empty] | SLUDGE UTILIZATION |  |  |  | SUMMARY DATA | [11 empty] | HIGH WEEKLY AVERAGE VALUES
|  | Total | Maxim. | Minim. | [8 empty] | Hypo - | [37 empty] | Stored |  |  |  | LOADING |  |  | CONCENTRATION |  |  |  | REPORTING |  |  |  | BOD |  | TSS |  |  | SETTLEABLE SOLIDS
| Totalizer | Flow | Flow | Flow | Flow | Holding | Septic |  | Average | Total | Grit |  | chlorite | Chlorine | [18 empty] | CBOD | [7 empty] | Quantity | Feed | Filter |  | Cake | Sludge | Lime | Average | Quantity |  | or |  |  |  | Monthly | Daily |  | Mo Aver | High Wkly | Daily |  |  |  | Sample
Date | Reading | Treated | (instant.) | (instant.) | By-passed | Received | Added | Conditions | Temp. | Precip. | Removed |  | Used | Residual | E. Coli | Influent | Primary | Effluent | Influent | Primary | Effluent |  | Influent | Primary | Effluent | Date | Influent | Influent | Primary | Primary | Effluent | Effluent | Effluent | Influent | Influent | Primary | Primary | Effluent | Effluent |  | Dewatered | Solids | Operation | Polymer | Dry Solid | Dewatered | Added | pH | Utilized | Site | Spread |  |  |  | Average | Maximum | Units | Minimum | Average | Maximum | Units | Exceptions | Frequency | Type |  | High Weekly Average |  | High Weekly Average |  |  | High Weekly Average
|  | (MG) | (MG) | (MG) | (MG) | (gallons) | (gallons) |  | (deg. F.) | (inches) | (cu. yd.) |  | (gallons) | (mg/L) | (#/100) | (s.u.) | (s.u.) | (s.u.) | (deg. C.) | (deg. C.) | (deg. C.) |  | (ml/L) | (ml/L) | (ml/L) |  | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) |  | (gallons) | (%) | (hours) | (lbs) | (%) | (cu. yd.) | (lbs) | (s.u.) | (cu. yd.) | [16 empty] | (mg / L) | (lbs / day) | (mg / L) | (lbs / day) |  | (mg / L)
7327567
1 | 7329923 | 2.356 |  |  | 0.00 |  |  | CLOUDY |  | 1.4 | [15 empty] | 1 | 325 | 6385.938 | 186 | 3654.7214 | 12 | 235.7885 | 10 | 354 | 6955.7602 | 104 | 2043.5002 | 19 | 373.3318 | [13 empty] | BOD, 5-day | Reporting : | 253.5098 | 366.1594 | (lbs / day) | 11.7143 | 13 | 15 | (mg / L) |  | 03/07 | 24 | Week 1 | 13 | 236 | 17 | 309 |  | 0 | check formulas for designation of weeks
2 | 7332066 | 2.143 |  |  | 0.00 |  |  | CLOUDY |  | 0.05 | [15 empty] | 2 | [26 empty] | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24
3 | 7334029 | 1.963 |  |  | 0.00 |  |  | CLOUDY |  | 0.12 | [15 empty] | 3 | [38 empty] | Week 2 | 12 | 240.5895 | 20.6667 | 412.4992 |  | #DIV/0! | identifies cell for keyed data entry
4 | 7336150 | 2.121 |  |  | 0.00 |  |  | CLOUDY |  | 0 |  |  |  |  | 4.1 | [10 empty] | 4
5 | 7338296 | 2.146 |  |  | 0.00 |  |  | CLEAR |  | 0 |  |  |  |  | 25.3 | [10 empty] | 5 | [38 empty] | Week 3 | 11.3333 | 272.3371 | 17 | 407.6842 |  | #DIV/0!
6 | 7340304 | 2.008 |  |  | 0.00 |  |  | LT RAIN |  | 0.3 |  |  |  |  | 2 | [10 empty] | 6 | 257 | 4303.907 |  |  | 11 | 184.2139 | 9 | 246 | 4119.6931 |  |  | 19 | 318.1877 | [13 empty] | pH | Reporting : | - | - | - | 0 | - | 0 | (s.u.) |  | 01/01 | GR
7 | 7342407 | 2.103 |  |  | 0.00 |  |  | LT RAIN |  | 0 | [15 empty] | 7 | 324 | 5682.6425 |  |  | 10 | 175.3902 | 7 | 314 | 5507.2523 |  |  | 18 | 315.7024 | [13 empty] | Effluent | Permit : | - | - | - | 6 | - | 8.5 | (s.u.) | - | 01/01 | GR | Week 4 |  |  | 20 | 391.5713 |  | #DIV/0!
8 | 7345302 | 2.895 |  |  | 0.00 |  |  | RAIN |  | 0.85 | [15 empty] | 8 | 224 | 5408.3232 | 164 | 3959.6652 | 15 | 362.1645 | 11 | 276 | 6663.8268 | 101 | 2438.5743 | 25 | 603.6075
9 | 7348500 | 3.198 |  |  | 0.00 |  |  | CLEAR |  | 0 | [15 empty] | 9 | [38 empty] | Week 5 | [5 empty] | #DIV/0!
10 | 7351151 | 2.651 |  |  | 0.00 |  |  | CLOUDY |  | 0 | [15 empty] | 10
11 | 7353674 | 2.523 |  |  | 0.00 |  |  | CLOUDY | [6 empty] | 1 | [10 empty] | 11 | [26 empty] | TSS | Reporting : | 400.8596 | 603.6075 | (lbs / day) | 19.2 | 20.6667 | 27 | (mg / L) |  | 03/07 | 24
12 | 7356322 | 2.648 |  |  | 0.00 |  |  | RAIN | [6 empty] | 387.3 | [10 empty] | 12 | [26 empty] | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24 | Maximum | 13 | 272.3371 | 20.6667 | 412.4992 |  | #DIV/0!
13 | 7359458 | 3.136 |  |  | 0.00 |  |  | CLEAR | [6 empty] | 10.9 | [10 empty] | 13 | 176 | 4603.1462 |  |  | 14 | 366.1594 | 11 | 186 | 4864.6886 |  |  | 20 | 523.0848
14 | 7362233 | 2.775 |  |  | 0.00 |  |  | CLEAR | [17 empty] | 14 | 176 | 4073.256 |  |  | 9 | 208.2915 | 6 | 178 | 4119.543 |  |  | 15 | 347.1525
15 | 7364877 | 2.644 |  |  | 0.00 |  |  | CLOUDY | [17 empty] | 15 | 195 | 4299.9372 | 142 | 3131.2363 | 11 | 242.5606 | 7 | 194 | 4277.8862 | 71 | 1565.6182 | 16 | 352.8154
16 | 7367578 | 2.701 |  |  | 0.00 |  |  | CLOUDY | [17 empty] | 16 | [26 empty] | SETTLEABLE
17 | 7370040 | 2.462 |  |  | 0.00 |  |  | CLEAR | [17 empty] | 17 | [26 empty] | SOLIDS | Reporting : | - | - | - | - | #DIV/0! | 0 | (mg / L) |  | 01/01 | GR
18 | 7372414 | 2.374 |  |  | 0.00 |  |  | CLEAR | [17 empty] | 18 | [26 empty] | Effluent | Permit : | - | - | - | - | (Report) | 0.3 | (mg / L) | - | 01/01 | GR
19 | 7374960 | 2.546 |  |  | 0.00 |  |  | CLOUDY | [6 empty] | 99 | [10 empty] | 19
20 | 7377361 | 2.401 |  |  | 0.00 |  |  | CLEAR | [6 empty] | 33.6 | [10 empty] | 20 | [7 empty] | 250 | 5006.085 |  |  | 13 | 260.3164
21 | 7379873 | 2.512 |  |  | 0.00 |  |  | CLEAR | [6 empty] | 5.2 | [10 empty] | 21 | [7 empty] | 254 | 5321.3203 |  |  | 20 | 419.0016
22 | 7382073 | 2.2 |  |  | 0.00 |  |  | CLEAR | [17 empty] | 22 | [7 empty] | 328 | 6018.144 | 100 | 1834.8 | 27 | 495.396 | [13 empty] | FLOW | Reporting : | 2.4775 | 3.198 | (MGD) | - | - | - | - |  | 99/99 | RC |  |  |  | CBOD
23 | [25 empty] | 23 | [26 empty] | Effluent | Permit : | 3.85 | (Report) | (MGD) | - | - | - | - | - | 99/99 | RC
24 | [25 empty] | 24 | [41 empty] | % Removal
25 | [25 empty] | 25
26 | [25 empty] | 26 | [41 empty] | 96.371
27 | [25 empty] | 27 | [26 empty] | BOD, 5-day | Reporting : | - | - | - | 94.8944 | - | - | (percent) |  | 01/30 | CA
28 | [25 empty] | 28 | [26 empty] | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
29 | [25 empty] | 29
30 | [25 empty] | 30
31 | [25 empty] | 31
[53 empty] | TSS | Reporting : | - | - | - | 92.5581 | - | - | (percent) |  | 01/30 | CA
Total | 54506 | 54.506 | - | - | 0 |  |  | - | - | 2.72 | 0.0 |  | 0 | - | - | - | - | - | - | - | - |  | - | - | - | Total | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  | - |  |  | - |  |  | - |  | - | - |  | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
Maximum | - | 3.198 |  |  | 0 |  |  | - |  | 1.4 | - |  | - | - | 387.3 | [10 empty] | Maximum | 325 | 6385.938 | 186 | 3959.6652 | 15 | 366.1594 | 11 | 354 | 6955.7602 | 104 | 2438.5743 | 27 | 603.6075 |  | - |  | - | - |  | - | - |  | - | - | -
Minimum | - | 1.963 |  |  | 0 |  |  | - |  | 0 | - |  | - | - | 1 | [10 empty] | Minimum | 176 | 4073.256 | 142 | 3131.2363 | 9 | 175.3902 | 6 | 178 | 4119.543 | 71 | 1565.6182 | 13 | 260.3164 |  | - |  | - | - |  | - | - |  | - | - | -
Average | - | 2.4775 |  |  | 0.000 |  |  | - |  | 0.272 | - |  | - | - | - | [10 empty] | Average | 239.5714 | 4965.3072 | 164 | 3581.8743 | 11.7143 | 253.5098 | 8.7143 | 258 | 5285.42 | 94 | 1970.6232 | 19.2 | 400.8596 | [10 empty] | - | -
[13 empty] | Geometric Mean : |  | 13.5255 | [14 empty] | Percent Removal : |  | 94.8944 |  |  |  | Percent Removal : |  | 92.5581

## September 08
BRUNSWICK SEWER DISTRICT | [11 empty] | State Discharge License Number W 002600-5L-C-R | [9 empty] | Certifying Official: |  |  | Francis E. McVey | BRUNSWICK SEWER DISTRICT | [13 empty] | State Discharge License Number W 002600-5L-C-R | [11 empty] | BRUNSWICK SEWER DISTRICT | [9 empty] | State Discharge License Number W 002600-5L-C-R
Monthly Report of Treatment Operations : |  |  |  |  | September | 2008 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [12 empty] | General Manager | Monthly Report of Treatment Operations : |  |  |  |  | September | 2008 | [7 empty] | N.P.D.E.S. Permit Number ME 0100102 | [9 empty] | Page 2. |  | Monthly Report of Treatment Operations : |  |  | September | 2008 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [7 empty] | Page 3.
SETTLEABLE
| FLOW | [6 empty] | WEATHER |  |  |  |  | DISINFECTION |  |  | P.H. |  |  | TEMPERATURE |  |  |  | SOLIDS |  |  |  | BIOCHEMICAL OXYGEN DEMAND | [6 empty] | TOTAL SUSPENDED SOLIDS | [6 empty] | SLUDGE DEWATERING | [7 empty] | SLUDGE UTILIZATION |  |  |  | SUMMARY DATA | [11 empty] | HIGH WEEKLY AVERAGE VALUES
|  | Total | Maxim. | Minim. | [8 empty] | Hypo - | [37 empty] | Stored |  |  |  | LOADING |  |  | CONCENTRATION |  |  |  | REPORTING |  |  |  | BOD |  | TSS |  |  | SETTLEABLE SOLIDS
| Totalizer | Flow | Flow | Flow | Flow | Holding | Septic |  | Average | Total | Grit |  | chlorite | Chlorine | [18 empty] | CBOD | [7 empty] | Quantity | Feed | Filter |  | Cake | Sludge | Lime | Average | Quantity |  | or |  |  |  | Monthly | Daily |  | Mo Aver | High Wkly | Daily |  |  |  | Sample
Date | Reading | Treated | (instant.) | (instant.) | By-passed | Received | Added | Conditions | Temp. | Precip. | Removed |  | Used | Residual | E. Coli | Influent | Primary | Effluent | Influent | Primary | Effluent |  | Influent | Primary | Effluent | Date | Influent | Influent | Primary | Primary | Effluent | Effluent | Effluent | Influent | Influent | Primary | Primary | Effluent | Effluent |  | Dewatered | Solids | Operation | Polymer | Dry Solid | Dewatered | Added | pH | Utilized | Site | Spread |  |  |  | Average | Maximum | Units | Minimum | Average | Maximum | Units | Exceptions | Frequency | Type |  | High Weekly Average |  | High Weekly Average |  |  | High Weekly Average
|  | (MG) | (MG) | (MG) | (MG) | (gallons) | (gallons) |  | (deg. F.) | (inches) | (cu. yd.) |  | (gallons) | (mg/L) | (#/100) | (s.u.) | (s.u.) | (s.u.) | (deg. C.) | (deg. C.) | (deg. C.) |  | (ml/L) | (ml/L) | (ml/L) |  | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) |  | (gallons) | (%) | (hours) | (lbs) | (%) | (cu. yd.) | (lbs) | (s.u.) | (cu. yd.) | [16 empty] | (mg / L) | (lbs / day) | (mg / L) | (lbs / day) |  | (mg / L)
1 | [25 empty] | 1 | [26 empty] | BOD, 5-day | Reporting : |  | 0 | (lbs / day) |  |  | 0 | (mg / L) |  | 03/07 | 24 | Week 1 | [5 empty] | 0 | check formulas for designation of weeks
2 | [25 empty] | 2 | [26 empty] | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24
3 | [25 empty] | 3 | [38 empty] | Week 2 | [5 empty] | #DIV/0! | identifies cell for keyed data entry
4 | [25 empty] | 4
5 | [25 empty] | 5 | [38 empty] | Week 3 | [5 empty] | #DIV/0!
6 | [25 empty] | 6 | [26 empty] | pH | Reporting : | - | - | - | 0 | - | 0 | (s.u.) |  | 01/01 | GR
7 | [25 empty] | 7 | [26 empty] | Effluent | Permit : | - | - | - | 6 | - | 8.5 | (s.u.) | - | 01/01 | GR | Week 4 | [5 empty] | #DIV/0!
8 | [25 empty] | 8
9 | [25 empty] | 9 | [38 empty] | Week 5
10 | [25 empty] | 10
11 | [25 empty] | 11 | [26 empty] | TSS | Reporting : |  | 0 | (lbs / day) |  |  | 0 | (mg / L) |  | 03/07 | 24
12 | [25 empty] | 12 | [26 empty] | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24 | Maximum | [5 empty] | #DIV/0!
13 | [25 empty] | 13
14 | [25 empty] | 14
15 | [25 empty] | 15
16 | [25 empty] | 16 | [26 empty] | SETTLEABLE
17 | [25 empty] | 17 | [26 empty] | SOLIDS | Reporting : | - | - | - | - | #DIV/0! | 0 | (mg / L) |  | 01/01 | GR
18 | [25 empty] | 18 | [26 empty] | Effluent | Permit : | - | - | - | - | (Report) | 0.3 | (mg / L) | - | 01/01 | GR
19 | [25 empty] | 19
20 | [25 empty] | 20
21 | [25 empty] | 21
22 | [25 empty] | 22 | [26 empty] | FLOW | Reporting : |  |  | (MGD) | - | - | - | - |  | 99/99 | RC |  |  |  | CBOD
23 | [25 empty] | 23 | [26 empty] | Effluent | Permit : | 3.85 | (Report) | (MGD) | - | - | - | - | - | 99/99 | RC
24 | [25 empty] | 24 | [41 empty] | % Removal
25 | [25 empty] | 25
26 | [25 empty] | 26
27 | [25 empty] | 27 | [26 empty] | BOD, 5-day | Reporting : | - | - | - |  | - | - | (percent) |  | 01/30 | CA
28 | [25 empty] | 28 | [26 empty] | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
29 | [25 empty] | 29
30 | [25 empty] | 30
31 | [25 empty] | 31
[53 empty] | TSS | Reporting : | - | - | - |  | - | - | (percent) |  | 01/30 | CA
Total |  |  | - | - | 0 |  |  | - | - |  | 0.0 |  | 0 | - | - | - | - | - | - | - | - |  | - | - | - | Total | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  | - |  |  | - |  |  | - |  | - | - |  | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
Maximum | - |  |  |  | 0 |  |  | - |  |  | - |  | - | - | - | [10 empty] | Maximum | [14 empty] | - |  | - | - |  | - | - |  | - | - | -
Minimum | - |  |  |  | 0 |  |  | - |  |  | - |  | - | - | - | [10 empty] | Minimum | [14 empty] | - |  | - | - |  | - | - |  | - | - | -
Average | - |  |  |  | 0.000 |  |  | - |  |  | - |  | - | - | - | [10 empty] | Average | [23 empty] | - | -
[13 empty] | Geometric Mean : |  | - | [14 empty] | Percent Removal : | [5 empty] | Percent Removal :

## October 08
BRUNSWICK SEWER DISTRICT | [11 empty] | State Discharge License Number W 002600-5L-C-R | [9 empty] | Certifying Official: |  |  | Francis E. McVey | BRUNSWICK SEWER DISTRICT | [13 empty] | State Discharge License Number W 002600-5L-C-R | [11 empty] | BRUNSWICK SEWER DISTRICT | [9 empty] | State Discharge License Number W 002600-5L-C-R
Monthly Report of Treatment Operations : |  |  |  |  | October | 2008 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [12 empty] | General Manager | Monthly Report of Treatment Operations : |  |  |  |  | October | 2008 | [7 empty] | N.P.D.E.S. Permit Number ME 0100102 | [9 empty] | Page 2. |  | Monthly Report of Treatment Operations : |  |  | October | 2008 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [7 empty] | Page 3.
SETTLEABLE
| FLOW | [6 empty] | WEATHER |  |  |  |  | DISINFECTION |  |  | P.H. |  |  | TEMPERATURE |  |  |  | SOLIDS |  |  |  | BIOCHEMICAL OXYGEN DEMAND | [6 empty] | TOTAL SUSPENDED SOLIDS | [6 empty] | SLUDGE DEWATERING | [7 empty] | SLUDGE UTILIZATION |  |  |  | SUMMARY DATA | [11 empty] | HIGH WEEKLY AVERAGE VALUES
|  | Total | Maxim. | Minim. | [8 empty] | Hypo - | [37 empty] | Stored |  |  |  | LOADING |  |  | CONCENTRATION |  |  |  | REPORTING |  |  |  | BOD |  | TSS |  |  | SETTLEABLE SOLIDS
| Totalizer | Flow | Flow | Flow | Flow | Holding | Septic |  | Average | Total | Grit |  | chlorite | Chlorine | [18 empty] | CBOD | [7 empty] | Quantity | Feed | Filter |  | Cake | Sludge | Lime | Average | Quantity |  | or |  |  |  | Monthly | Daily |  | Mo Aver | High Wkly | Daily |  |  |  | Sample
Date | Reading | Treated | (instant.) | (instant.) | By-passed | Received | Added | Conditions | Temp. | Precip. | Removed |  | Used | Residual | E. Coli | Influent | Primary | Effluent | Influent | Primary | Effluent |  | Influent | Primary | Effluent | Date | Influent | Influent | Primary | Primary | Effluent | Effluent | Effluent | Influent | Influent | Primary | Primary | Effluent | Effluent |  | Dewatered | Solids | Operation | Polymer | Dry Solid | Dewatered | Added | pH | Utilized | Site | Spread |  |  |  | Average | Maximum | Units | Minimum | Average | Maximum | Units | Exceptions | Frequency | Type |  | High Weekly Average |  | High Weekly Average |  |  | High Weekly Average
|  | (MG) | (MG) | (MG) | (MG) | (gallons) | (gallons) |  | (deg. F.) | (inches) | (cu. yd.) |  | (gallons) | (mg/L) | (#/100) | (s.u.) | (s.u.) | (s.u.) | (deg. C.) | (deg. C.) | (deg. C.) |  | (ml/L) | (ml/L) | (ml/L) |  | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) |  | (gallons) | (%) | (hours) | (lbs) | (%) | (cu. yd.) | (lbs) | (s.u.) | (cu. yd.) | [16 empty] | (mg / L) | (lbs / day) | (mg / L) | (lbs / day) |  | (mg / L)
1 | [25 empty] | 1 | [26 empty] | BOD, 5-day | Reporting : |  | 0 | (lbs / day) |  |  | 0 | (mg / L) |  | 03/07 | 24 | Week 1 | [5 empty] | 0 | check formulas for designation of weeks
2 | [25 empty] | 2 | [26 empty] | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24
3 | [12 empty] | O | O | O | [10 empty] | 3 | [38 empty] | Week 2 | [5 empty] | d | identifies cell for keyed data entry
4 | [25 empty] | 4
5 | [12 empty] | F | F | F | [10 empty] | 5 | [38 empty] | Week 3 | [5 empty] | #DIV/0!
6 | [25 empty] | 6 | [26 empty] | pH | Reporting : | - | - | - | 0 | - | 0 | (s.u.) |  | 01/01 | GR
7 | [12 empty] | F | F | F | [10 empty] | 7 | [26 empty] | Effluent | Permit : | - | - | - | 6 | - | 8.5 | (s.u.) | - | 01/01 | GR | Week 4 | [5 empty] | #DIV/0!
8 | [25 empty] | 8
9 | [25 empty] | 9 | [38 empty] | Week 5
10 | [25 empty] | 10
11 | [12 empty] | F | F | F | [10 empty] | 11 | [26 empty] | TSS | Reporting : |  | 0 | (lbs / day) |  |  | 0 | (mg / L) |  | 03/07 | 24
12 | [25 empty] | 12 | [26 empty] | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24 | Maximum | [5 empty] | #DIV/0!
13 | [12 empty] | O | O | O | [10 empty] | 13
14 | [25 empty] | 14
15 | [12 empty] | R | R | R | [10 empty] | 15
16 | [25 empty] | 16 | [26 empty] | SETTLEABLE
17 | [25 empty] | 17 | [26 empty] | SOLIDS | Reporting : | - | - | - | - | #DIV/0! | 0 | (mg / L) |  | 01/01 | GR
18 | [25 empty] | 18 | [26 empty] | Effluent | Permit : | - | - | - | - | (Report) | 0.3 | (mg / L) | - | 01/01 | GR
19 | [12 empty] | S | S | S | [10 empty] | 19
20 | [25 empty] | 20
21 | [12 empty] | E | E | E | [10 empty] | 21
22 | [25 empty] | 22 | [26 empty] | FLOW | Reporting : |  |  | (MGD) | - | - | - | - |  | 99/99 | RC |  |  |  | CBOD
23 | [12 empty] | A | A | A | [10 empty] | 23 | [26 empty] | Effluent | Permit : | 3.85 | (Report) | (MGD) | - | - | - | - | - | 99/99 | RC
24 | [25 empty] | 24 | [41 empty] | % Removal
25 | [12 empty] | S | S | S | [10 empty] | 25
26 | [25 empty] | 26
27 | [12 empty] | O | O | O | [10 empty] | 27 | [26 empty] | BOD, 5-day | Reporting : | - | - | - |  | - | - | (percent) |  | 01/30 | CA
28 | [25 empty] | 28 | [26 empty] | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
29 | [12 empty] | N | N | N | [10 empty] | 29
30 | [25 empty] | 30
31 | [25 empty] | 31
[53 empty] | TSS | Reporting : | - | - | - |  | - | - | (percent) |  | 01/30 | CA
Total |  |  | - | - | 0 |  |  | - | - |  | 0.0 |  | 0 | - | - | - | - | - | - | - | - |  | - | - | - | Total | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  | - |  |  | - |  |  | - |  | - | - |  | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
Maximum | - |  |  |  | 0 |  |  | - |  |  | - |  | - | - | - | [10 empty] | Maximum | [14 empty] | - |  | - | - |  | - | - |  | - | - | -
Minimum | - |  |  |  | 0 |  |  | - |  |  | - |  | - | - | - | [10 empty] | Minimum | [14 empty] | - |  | - | - |  | - | - |  | - | - | -
Average | - |  |  |  | 0.000 |  |  | - |  |  | - |  | - | - | - | [10 empty] | Average | [23 empty] | - | -
[13 empty] | Geometric Mean : |  | - | [14 empty] | Percent Removal : | [5 empty] | Percent Removal :

## November 08
BRUNSWICK SEWER DISTRICT | [11 empty] | State Discharge License Number W 002600-5L-C-R | [9 empty] | Certifying Official: |  |  | Francis E. McVey | BRUNSWICK SEWER DISTRICT | [13 empty] | State Discharge License Number W 002600-5L-C-R | [11 empty] | BRUNSWICK SEWER DISTRICT | [9 empty] | State Discharge License Number W 002600-5L-C-R
Monthly Report of Treatment Operations : |  |  |  |  | November | 2008 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [12 empty] | General Manager | Monthly Report of Treatment Operations : |  |  |  |  | November | 2008 | [7 empty] | N.P.D.E.S. Permit Number ME 0100102 | [9 empty] | Page 2. |  | Monthly Report of Treatment Operations : |  |  | November | 2008 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [7 empty] | Page 3.
SETTLEABLE
| FLOW | [6 empty] | WEATHER |  |  |  |  | DISINFECTION |  |  | P.H. |  |  | TEMPERATURE |  |  |  | SOLIDS |  |  |  | BIOCHEMICAL OXYGEN DEMAND | [6 empty] | TOTAL SUSPENDED SOLIDS | [6 empty] | SLUDGE DEWATERING | [7 empty] | SLUDGE UTILIZATION |  |  |  | SUMMARY DATA | [11 empty] | HIGH WEEKLY AVERAGE VALUES
|  | Total | Maxim. | Minim. | [8 empty] | Hypo - | [37 empty] | Stored |  |  |  | LOADING |  |  | CONCENTRATION |  |  |  | REPORTING |  |  |  | BOD |  | TSS |  |  | SETTLEABLE SOLIDS
| Totalizer | Flow | Flow | Flow | Flow | Holding | Septic |  | Average | Total | Grit |  | chlorite | Chlorine | [18 empty] | CBOD | [7 empty] | Quantity | Feed | Filter |  | Cake | Sludge | Lime | Average | Quantity |  | or |  |  |  | Monthly | Daily |  | Mo Aver | High Wkly | Daily |  |  |  | Sample
Date | Reading | Treated | (instant.) | (instant.) | By-passed | Received | Added | Conditions | Temp. | Precip. | Removed |  | Used | Residual | E. Coli | Influent | Primary | Effluent | Influent | Primary | Effluent |  | Influent | Primary | Effluent | Date | Influent | Influent | Primary | Primary | Effluent | Effluent | Effluent | Influent | Influent | Primary | Primary | Effluent | Effluent |  | Dewatered | Solids | Operation | Polymer | Dry Solid | Dewatered | Added | pH | Utilized | Site | Spread |  |  |  | Average | Maximum | Units | Minimum | Average | Maximum | Units | Exceptions | Frequency | Type |  | High Weekly Average |  | High Weekly Average |  |  | High Weekly Average
|  | (MG) | (MG) | (MG) | (MG) | (gallons) | (gallons) |  | (deg. F.) | (inches) | (cu. yd.) |  | (gallons) | (mg/L) | (#/100) | (s.u.) | (s.u.) | (s.u.) | (deg. C.) | (deg. C.) | (deg. C.) |  | (ml/L) | (ml/L) | (ml/L) |  | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) |  | (gallons) | (%) | (hours) | (lbs) | (%) | (cu. yd.) | (lbs) | (s.u.) | (cu. yd.) | [16 empty] | (mg / L) | (lbs / day) | (mg / L) | (lbs / day) |  | (mg / L)
1 | [25 empty] | 1 | [26 empty] | BOD, 5-day | Reporting : |  | 0 | (lbs / day) |  |  | 0 | (mg / L) |  | 03/07 | 24 | Week 1 | [5 empty] | 0 | check formulas for designation of weeks
2 | [25 empty] | 2 | [26 empty] | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24
3 | [12 empty] | O | O | O | [10 empty] | 3 | [38 empty] | Week 2 | [5 empty] | #DIV/0! | identifies cell for keyed data entry
4 | [25 empty] | 4
5 | [12 empty] | F | F | F | [10 empty] | 5 | [38 empty] | Week 3 | [5 empty] | #DIV/0!
6 | [25 empty] | 6 | [26 empty] | pH | Reporting : | - | - | - | 0 | - | 0 | (s.u.) |  | 01/01 | GR
7 | [12 empty] | F | F | F | [10 empty] | 7 | [26 empty] | Effluent | Permit : | - | - | - | 6 | - | 8.5 | (s.u.) | - | 01/01 | GR | Week 4 | [5 empty] | #DIV/0!
8 | [25 empty] | 8
9 | [25 empty] | 9 | [38 empty] | Week 5
10 | [25 empty] | 10
11 | [12 empty] | F | F | F | [10 empty] | 11 | [26 empty] | TSS | Reporting : |  | 0 | (lbs / day) |  |  | 0 | (mg / L) |  | 03/07 | 24
12 | [25 empty] | 12 | [26 empty] | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24 | Maximum | [5 empty] | #DIV/0!
13 | [12 empty] | O | O | O | [10 empty] | 13
14 | [25 empty] | 14
15 | [12 empty] | R | R | R | [10 empty] | 15
16 | [25 empty] | 16 | [26 empty] | SETTLEABLE
17 | [25 empty] | 17 | [26 empty] | SOLIDS | Reporting : | - | - | - | - | #DIV/0! | 0 | (mg / L) |  | 01/01 | GR
18 | [25 empty] | 18 | [26 empty] | Effluent | Permit : | - | - | - | - | (Report) | 0.3 | (mg / L) | - | 01/01 | GR
19 | [12 empty] | S | S | S | [10 empty] | 19
20 | [25 empty] | 20
21 | [12 empty] | E | E | E | [10 empty] | 21
22 | [25 empty] | 22 | [26 empty] | FLOW | Reporting : |  |  | (MGD) | - | - | - | - |  | 99/99 | RC |  |  |  | CBOD
23 | [12 empty] | A | A | A | [10 empty] | 23 | [26 empty] | Effluent | Permit : | 3.85 | (Report) | (MGD) | - | - | - | - | - | 99/99 | RC
24 | [25 empty] | 24 | [41 empty] | % Removal
25 | [12 empty] | S | S | S | [10 empty] | 25
26 | [25 empty] | 26
27 | [12 empty] | O | O | O | [10 empty] | 27 | [26 empty] | BOD, 5-day | Reporting : | - | - | - |  | - | - | (percent) |  | 01/30 | CA
28 | [25 empty] | 28 | [26 empty] | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
29 | [12 empty] | N | N | N | [10 empty] | 29
30 | [25 empty] | 30
31 | [25 empty] | 31
[53 empty] | TSS | Reporting : | - | - | - |  | - | - | (percent) |  | 01/30 | CA
Total |  |  | - | - | 0 |  |  | - | - |  | 0.0 |  | 0 | - | - | - | - | - | - | - | - |  | - | - | - | Total | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  | - |  |  | - |  |  | - |  | - | - |  | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
Maximum | - |  |  |  | 0 |  |  | - |  |  | - |  | - | - | - | [10 empty] | Maximum | [14 empty] | - |  | - | - |  | - | - |  | - | - | -
Minimum | - |  |  |  | 0 |  |  | - |  |  | - |  | - | - | - | [10 empty] | Minimum | [14 empty] | - |  | - | - |  | - | - |  | - | - | -
Average | - |  |  |  | 0.000 |  |  | - |  |  | - |  | - | - | - | [10 empty] | Average | [23 empty] | - | -
[13 empty] | Geometric Mean : |  | - | [14 empty] | Percent Removal : | [5 empty] | Percent Removal :

## December 08
BRUNSWICK SEWER DISTRICT | [11 empty] | State Discharge License Number W 002600-5L-C-R | [9 empty] | Certifying Official: |  |  | Francis E. McVey | BRUNSWICK SEWER DISTRICT | [13 empty] | State Discharge License Number W 002600-5L-C-R | [11 empty] | BRUNSWICK SEWER DISTRICT | [9 empty] | State Discharge License Number W 002600-5L-C-R
Monthly Report of Treatment Operations : |  |  |  |  | December | 2008 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [12 empty] | General Manager | Monthly Report of Treatment Operations : |  |  |  |  | December | 2008 | [7 empty] | N.P.D.E.S. Permit Number ME 0100102 | [9 empty] | Page 2. |  | Monthly Report of Treatment Operations : |  |  | December | 2008 | [5 empty] | N.P.D.E.S. Permit Number ME 0100102 | [7 empty] | Page 3.
SETTLEABLE
| FLOW | [6 empty] | WEATHER |  |  |  |  | DISINFECTION |  |  | P.H. |  |  | TEMPERATURE |  |  |  | SOLIDS |  |  |  | BIOCHEMICAL OXYGEN DEMAND | [6 empty] | TOTAL SUSPENDED SOLIDS | [6 empty] | SLUDGE DEWATERING | [7 empty] | SLUDGE UTILIZATION |  |  |  | SUMMARY DATA | [11 empty] | HIGH WEEKLY AVERAGE VALUES
|  | Total | Maxim. | Minim. | [8 empty] | Hypo - | [37 empty] | Stored |  |  |  | LOADING |  |  | CONCENTRATION |  |  |  | REPORTING |  |  |  | BOD |  | TSS |  |  | SETTLEABLE SOLIDS
| Totalizer | Flow | Flow | Flow | Flow | Holding | Septic |  | Average | Total | Grit |  | chlorite | Chlorine | [18 empty] | CBOD | [7 empty] | Quantity | Feed | Filter |  | Cake | Sludge | Lime | Average | Quantity |  | or |  |  |  | Monthly | Daily |  | Mo Aver | High Wkly | Daily |  |  |  | Sample
Date | Reading | Treated | (instant.) | (instant.) | By-passed | Received | Added | Conditions | Temp. | Precip. | Removed |  | Used | Residual | E. Coli | Influent | Primary | Effluent | Influent | Primary | Effluent |  | Influent | Primary | Effluent | Date | Influent | Influent | Primary | Primary | Effluent | Effluent | Effluent | Influent | Influent | Primary | Primary | Effluent | Effluent |  | Dewatered | Solids | Operation | Polymer | Dry Solid | Dewatered | Added | pH | Utilized | Site | Spread |  |  |  | Average | Maximum | Units | Minimum | Average | Maximum | Units | Exceptions | Frequency | Type |  | High Weekly Average |  | High Weekly Average |  |  | High Weekly Average
|  | (MG) | (MG) | (MG) | (MG) | (gallons) | (gallons) |  | (deg. F.) | (inches) | (cu. yd.) |  | (gallons) | (mg/L) | (#/100) | (s.u.) | (s.u.) | (s.u.) | (deg. C.) | (deg. C.) | (deg. C.) |  | (ml/L) | (ml/L) | (ml/L) |  | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (mg/L) | (lbs) | (mg/L) | (lbs) | (mg/L) | (lbs) |  | (gallons) | (%) | (hours) | (lbs) | (%) | (cu. yd.) | (lbs) | (s.u.) | (cu. yd.) | [16 empty] | (mg / L) | (lbs / day) | (mg / L) | (lbs / day) |  | (mg / L)
1 | [25 empty] | 1 | [26 empty] | BOD, 5-day | Reporting : |  | 0 | (lbs / day) |  |  | 0 | (mg / L) |  | 03/07 | 24 | Week 1 | [5 empty] | 0 | check formulas for designation of weeks
2 | [25 empty] | 2 | [26 empty] | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24
3 | [12 empty] | O | O | O | [10 empty] | 3 | [38 empty] | Week 2 | [5 empty] | #DIV/0! | identifies cell for keyed data entry
4 | [25 empty] | 4
5 | [12 empty] | F | F | F | [10 empty] | 5 | [38 empty] | Week 3 | [5 empty] | #DIV/0!
6 | [25 empty] | 6 | [26 empty] | pH | Reporting : | - | - | - | 0 | - | 0 | (s.u.) |  | 01/01 | GR
7 | [12 empty] | F | F | F | [10 empty] | 7 | [26 empty] | Effluent | Permit : | - | - | - | 6 | - | 8.5 | (s.u.) | - | 01/01 | GR | Week 4 | [5 empty] | #DIV/0!
8 | [25 empty] | 8
9 | [25 empty] | 9 | [38 empty] | Week 5
10 | [25 empty] | 10
11 | [12 empty] | F | F | F | [10 empty] | 11 | [26 empty] | TSS | Reporting : |  | 0 | (lbs / day) |  |  | 0 | (mg / L) |  | 03/07 | 24
12 | [25 empty] | 12 | [26 empty] | Effluent | Permit : | 963 | 1605 | (lbs / day) | 30 | 45 | 50 | (mg / L) | - | 03/07 | 24 | Maximum | [5 empty] | #DIV/0!
13 | [12 empty] | O | O | O | [10 empty] | 13
14 | [25 empty] | 14
15 | [12 empty] | R | R | R | [10 empty] | 15
16 | [25 empty] | 16 | [26 empty] | SETTLEABLE
17 | [25 empty] | 17 | [26 empty] | SOLIDS | Reporting : | - | - | - | - | #DIV/0! | 0 | (mg / L) |  | 01/01 | GR
18 | [25 empty] | 18 | [26 empty] | Effluent | Permit : | - | - | - | - | (Report) | 0.3 | (mg / L) | - | 01/01 | GR
19 | [12 empty] | S | S | S | [10 empty] | 19
20 | [25 empty] | 20
21 | [12 empty] | E | E | E | [10 empty] | 21
22 | [25 empty] | 22 | [26 empty] | FLOW | Reporting : |  |  | (MGD) | - | - | - | - |  | 99/99 | RC |  |  |  | CBOD
23 | [12 empty] | A | A | A | [10 empty] | 23 | [26 empty] | Effluent | Permit : | 3.85 | (Report) | (MGD) | - | - | - | - | - | 99/99 | RC
24 | [25 empty] | 24 | [41 empty] | % Removal
25 | [12 empty] | S | S | S | [10 empty] | 25
26 | [25 empty] | 26
27 | [12 empty] | O | O | O | [10 empty] | 27 | [26 empty] | BOD, 5-day | Reporting : | - | - | - |  | - | - | (percent) |  | 01/30 | CA
28 | [25 empty] | 28 | [26 empty] | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
29 | [12 empty] | N | N | N | [10 empty] | 29
30 | [25 empty] | 30
31 | [25 empty] | 31
[53 empty] | TSS | Reporting : | - | - | - |  | - | - | (percent) |  | 01/30 | CA
Total |  |  | - | - | 0 |  |  | - | - |  | 0.0 |  | 0 | - | - | - | - | - | - | - | - |  | - | - | - | Total | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  | - |  |  | - |  |  | - |  | - | - |  | % removal | Permit : | - | - | - | 85 | - | - | (percent) | - | 01/30 | CA
Maximum | - |  |  |  | 0 |  |  | - |  |  | - |  | - | - | - | [10 empty] | Maximum | [14 empty] | - |  | - | - |  | - | - |  | - | - | -
Minimum | - |  |  |  | 0 |  |  | - |  |  | - |  | - | - | - | [10 empty] | Minimum | [14 empty] | - |  | - | - |  | - | - |  | - | - | -
Average | - |  |  |  | 0.000 |  |  | - |  |  | - |  | - | - | - | [10 empty] | Average | [23 empty] | - | -
[13 empty] | Geometric Mean : |  | - | [14 empty] | Percent Removal : | [5 empty] | Percent Removal :

## ANNUAL 08
BRUNSWICK SEWER DISTRICT | [9 empty] | State Discharge License Number W 002600-5L-C-R | [9 empty] | Gregory H. Thulen
Monthly Report of Treatment Operations : | [21 empty] | 0 | 0 | 0 | 0
Annual Report of Treatment Operations: 2008. | [9 empty] | N.P.D.E.S. Permit Number ME 0100102 | [9 empty] | Treatment Operations Division Supervisor
'file:///tmp/in/input.xls'#$ANNUAL 08 | [19 empty] | Page 1.
[17 empty] | A N N U A L |  |  | P E R M I T
| Parameter |  | Function | Units | JANUARY | FEBRUARY | MARCH | APRIL | MAY | JUNE | JULY | AUGUST | SEPTEMBER | OCTOBER | NOVEMBER | DECEMBER | Total | Max/Avg/Min | Units | Limits
| PLANT FLOW |  | total | (mg) | 78.032 | 92.491 | 119.593 | 123.4 | 114.669 | 72.524 | 63.786 | 54.506 |  |  |  |  | 719.001 | 89.8751 | (mg) |  | total; average
|  |  | maximum | (mgd) | 3.123 | 5.253 | 5.024 | 7.132 | 6.17 | 2.963 | 2.361 | 3.198 |  |  |  |  | - | 7.132 | (mgd) | Report only. | max
|  |  | average | (mgd) | 2.5172 | 3.1893 | 3.8578 | 4.1133 | 3.699 | 2.4175 | 2.0576 | 2.4775 |  |  |  |  | - | 3.0412 | (mgd) | 3.85 | average
|  |  | minimum | (mgd) | 2.065 | 2.346 | 2.838 | 3.025 | 2.676 | 2.082 | 1.914 | 1.963 |  |  |  |  | - | 1.914 | (mgd) |  | min
| HOLDING WASTE |  | total received | (gallons) | JANUARY: 45550; FEBRUARY: 28200; MARCH: 27900; APRIL: 72300; MAY: 102900; JUNE: 96100; JULY: 77450 | 450400 | 64342.8571 | (gallons) |  | total; average
| SEPTIC WASTE |  | total received | (gallons) | JANUARY: 32750; FEBRUARY: 23750; MARCH: 39750; APRIL: 134000; MAY: 179050; JUNE: 229050; JULY: 207200 | 845550 | 120792.8571 | (gallons) |  | total; average
| GRIT |  | total removed | (cubic yards) | 0.0 | 0.0 | 4 | 0.0 | 0.0 | 0.0 | 6 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 10 | 5 | (cubic yards) |  | total; per month
| DISINFECTION |  | hypochlorite | (gallons) | 0 | 0 | 0 | 0 | 542.5 | 793.5 | 670.3 | 0 | 0 | 0 | 0 | 0 | 2006.3 | 668.7667 | (gallons) |  | total; average
| pH | Influent | maximum | (std units) | JANUARY: 7.55; FEBRUARY: 7.11; MARCH: 6.92; APRIL: 7.04; MAY: 7.17; JUNE: 7.26; JULY: 7.45 | - | 7.55 |  |  | max
|  |  | average |  | JANUARY: 6.9803; FEBRUARY: 6.6379; MARCH: 6.5268; APRIL: 6.7347; MAY: 6.8729; JUNE: 6.9803; JULY: 7.1919 | - | 6.8464 | (std units) |  | average
|  |  | minimum |  | JANUARY: 6.27; FEBRUARY: 6.06; MARCH: 5.9; APRIL: 5.76; MAY: 6.59; JUNE: 6.6; JULY: 6.79 | - | 5.76 |  |  | min
|  | Primary | maximum | (std units) | JANUARY: 8.32; FEBRUARY: 7.16; MARCH: 7.4; APRIL: 6.91; MAY: 7.09; JUNE: 7.46; JULY: 8.2 | - | - |  |  | max
|  |  | average |  | JANUARY: 7.2723; FEBRUARY: 6.7859; MARCH: 6.6606; APRIL: 6.698; MAY: 6.8506; JUNE: 7.091; JULY: 7.3145 | - | 6.9533 | (std units) |  | average
|  |  | minimum |  | JANUARY: 6.71; FEBRUARY: 5.59; MARCH: 6.05; APRIL: 6.02; MAY: 6.68; JUNE: 6.05; JULY: 6.39 | - | - |  |  | min
|  | Effluent | maximum | (std units) | JANUARY: 7.18; FEBRUARY: 7.01; MARCH: 7.07; APRIL: 6.95; MAY: 6.9; JUNE: 6.62; JULY: 7.12 | - | 7.18 |  | 9 | max
|  |  | average |  | JANUARY: 6.8029; FEBRUARY: 6.7155; MARCH: 6.6668; APRIL: 6.676; MAY: 6.6384; JUNE: 6.3303; JULY: 6.8148 | - | 6.6635 | (std units) |  | average
|  |  | minimum |  | JANUARY: 6.21; FEBRUARY: 6.09; MARCH: 6.11; APRIL: 6.07; MAY: 6.12; JUNE: 6.03; JULY: 6.33 | - | 6.03 |  | 6 | min
TEMPERATURE
|  | Influent | maximum | (degrees C.) | JANUARY: 12.8; FEBRUARY: 12; MARCH: 10.6; APRIL: 11.6; MAY: 13.7; JUNE: 16.4; JULY: 18.5 | - | 18.5 |  |  | max
|  |  | average |  | JANUARY: 11.3097; FEBRUARY: 10.4759; MARCH: 9.7774; APRIL: 10.39; MAY: 12.371; JUNE: 14.7267; JULY: 16.671 | - | 12.2459 | (degrees C.) |  | average
|  |  | minimum |  | JANUARY: 10.4; FEBRUARY: 9.2; MARCH: 8.3; APRIL: 9.2; MAY: 11.1; JUNE: 13.1; JULY: 14.7 | - | 8.3 |  |  | min
|  | Primary | maximum | (degrees C.) | JANUARY: 11.8; FEBRUARY: 12.9; MARCH: 10.4; APRIL: 12.1; MAY: 14.4; JUNE: 16.3; JULY: 18.4 | - | - |  |  | max
|  |  | average |  | JANUARY: 10.3677; FEBRUARY: 9.6241; MARCH: 8.8871; APRIL: 10.0567; MAY: 12.3581; JUNE: 14.8467; JULY: 17.0452 | - | 11.8836 | (degrees C.) |  | average
|  |  | minimum |  | JANUARY: 8.3; FEBRUARY: 8.3; MARCH: 7.6; APRIL: 8.9; MAY: 10.8; JUNE: 13.5; JULY: 15.7 | - | - |  |  | min
|  | Effluent | maximum | (degrees C.) | JANUARY: 12.3; FEBRUARY: 11.9; MARCH: 10.9; APRIL: 12.8; MAY: 15.8; JUNE: 17.9; JULY: 20 | - | 20 |  |  | max
|  |  | average |  | JANUARY: 9.6097; FEBRUARY: 9.1621; MARCH: 9.0968; APRIL: 10.7533; MAY: 13.2194; JUNE: 16.2267; JULY: 18.5774 | - | 12.3779 | (degrees C.) |  | average
|  |  | minimum |  | JANUARY: 7; FEBRUARY: 7.5; MARCH: 6.7; APRIL: 9.4; MAY: 11.2; JUNE: 15; JULY: 16.8 | - | 6.7 |  |  | min
SETTLEABLE SOLIDS
|  | Influent | maximum | (ml / l) | JANUARY: 18; FEBRUARY: 10; MARCH: 6.5; APRIL: 13; MAY: 7.5; JUNE: 17; JULY: 12 | - | 18 |  |  | max
|  |  | average |  | JANUARY: 6.1774; FEBRUARY: 4.7586; MARCH: 3.4194; APRIL: 4.2667; MAY: 4.4839; JUNE: 6.9667; JULY: 7.371 | - | 5.3491 | (ml / l) |  | average
|  |  | minimum |  | JANUARY: 1.5; FEBRUARY: 1; MARCH: 1; APRIL: 2; MAY: 1; JUNE: 2.5; JULY: 2 | - | 1 |  |  | min
|  | Primary | maximum | (ml / l) | JANUARY: 0.2; FEBRUARY: 2.5; MARCH: 0.5; APRIL: 1.5; MAY: 1; JUNE: 1.5; JULY: 1.5 | - | - |  |  | max
|  |  | average |  | JANUARY: 0.03; FEBRUARY: 0.15552; MARCH: 0.079355; APRIL: 0.091333; MAY: 0.13677; JUNE: 0.4; JULY: 0.1913 | - | 0.1549 | (ml / l) |  | average
|  |  | minimum |  | JANUARY: 0; FEBRUARY: 0; MARCH: 0; APRIL: 0.01; MAY: 0.01; JUNE: 0.1; JULY: 0.1 | - | - |  |  | min
|  | Effluent | maximum | (ml / l) | JANUARY: 0.01; FEBRUARY: 0.01; MARCH: 0.01; APRIL: 0.1; MAY: 0.1; JUNE: 0.1; JULY: 0.1 | - | 0.1 |  | 0.3 | max
|  |  | average |  | JANUARY: 0.0022581; FEBRUARY: 0.0010345; MARCH: 0.0025806; APRIL: 0.0046667; MAY: 0.1; JUNE: 0.1; JULY: 0.1 | - | 0.044363 | (ml / l) |  | average
|  |  | minimum |  | JANUARY: 0; FEBRUARY: 0; MARCH: 0; APRIL: 0; MAY: 0.1; JUNE: 0.1; JULY: 0.1 | - | 0 |  |  | min
BRUNSWICK SEWER DISTRICT |  |  |  |  | JUNE: State Discharge License Number W 002600-5L-C-R |  |  |  | Gregory H. Thulen
Annual Report of Treatment Operations: 2008. |  |  |  |  | JUNE: N.P.D.E.S. Permit Number ME 0100102 |  |  |  | Treatment Operations Division Supervisor
'file:///tmp/in/input.xls'#$ANNUAL 08 | [19 empty] | Page 2.
[17 empty] | A N N U A L |  |  | P E R M I T
| Parameter |  | Function | Units | JANUARY | FEBRUARY | MARCH | APRIL | MAY | JUNE | JULY | AUGUST | SEPTEMBER | OCTOBER | NOVEMBER | DECEMBER | Total | Max/Avg/Min | Units | Limits
BIOCHEMICAL OXYGEN DEMAND
|  | Influent | maximum | (mg / l) | 245 | 246 | 196 | 169 | 280 | 311 | 331 | 325 |  |  |  |  | - | 331 |  |  | max
|  |  | average |  | 211.5 | 168.4615 | 135.75 | 127.7692 | 180.5 | 252.4167 | 280.0714 | 239.5714 |  |  |  |  | - | 199.505 | (mg / l) |  | average
|  |  | minimum |  | 135 | 112 | 98 | 83 | 89 | 201 | 222 | 176 |  |  |  |  | - | 83 |  |  | min
|  | Influent | maximum | (pounds) | 4745.2932 | 6469.5048 | 5556.1414 | 5394.4454 | 6384.4368 | 6001.9144 | 5690.6239 | 6385.938 |  |  |  |  | - | 6469.5048 |  |  | max
|  |  | average |  | 4398.4409 | 4440.8749 | 4386.6023 | 4452.0633 | 5290.7632 | 5101.1944 | 4932.8944 | 4965.3072 |  |  |  |  | - | 4746.0176 | (pounds) |  | average
|  |  | minimum |  | 3017.412 | 3794.4081 | 3190.2585 | 3212.568 | 3830.612 | 4066.8175 | 3812.1973 | 4073.256 |  |  |  |  | - | 3017.412 |  |  | min
|  | Primary | maximum | (mg / l) | 155 | 176 | 125 | 89 | 163 | 181 | 170 | 186 |  |  |  |  | - | - |  |  | max
|  |  | average |  | 146.75 | 133 | 103 | 78.5 | 124.2 | 155.75 | 149.75 | 164 |  |  |  |  | - | 131.8688 | (mg / l) |  | average
|  |  | minimum |  | 139 | 105 | 81 | 61 | 74 | 140 | 129 | 142 |  |  |  |  | - | - |  |  | min
|  | Primary | maximum | (pounds) | 3341.6295 | 3976.3786 | 3648.75 | 2911.6608 | 4245.9107 | 3493.0756 | 3104.982 | 3959.6652 |  |  |  |  | - | - |  |  | max
|  |  | average |  | 3089.6364 | 3357.5689 | 3063.9909 | 2584.7933 | 3624.941 | 3231.2016 | 2621.164 | 3581.8743 |  |  |  |  | - | 3144.3963 | (pounds) |  | average
|  |  | minimum |  | 2596.7424 | 3048.3117 | 2479.2318 | 2284.5262 | 3008.2547 | 3088.8274 | 2318.2281 | 3131.2363 |  |  |  |  | - | - |  |  | min
|  | Effluent | maximum | (mg / l) | 22 | 20 | 18 | 17 | 15 | 17 | 16 | 15 |  |  |  |  | - | 22 |  | 50 | max
|  |  | average |  | 16.7143 | 15.4615 | 13.9167 | 11.7692 | 12.3571 | 15.0833 | 11 | 11.7143 |  |  |  |  | - | 13.5021 | (mg / l) | 30 | average
|  |  | minimum |  | 12 | 12 | 8 | 8 | 8 | 13 | 8 | 9 |  |  |  |  | - | 8 |  |  | min
|  | Effluent | maximum | (pounds) | 457.1154 | 624.3991 | 676.2906 | 1011.175 | 566.0358 | 386.0669 | 272.8848 | 366.1594 |  |  |  |  | - | 1011.175 |  | 1605 | max
|  |  | average |  | 350.2764 | 415.2326 | 454.302 | 432.5676 | 382.0715 | 308.3798 | 194.0337 | 253.5098 |  |  |  |  | - | 348.7967 | (pounds) | 963 | average
|  |  | minimum |  | 224.5795 | 308.7468 | 263.7442 | 230.2507 | 273.6187 | 242.8608 | 137.3765 | 175.3902 |  |  |  |  | - | 137.3765 |  |  | min
|  | Effluent | removal | (percent) | 92.0364 | 90.6498 | 89.6434 | 90.2839 | 92.7785 | 93.9548 | 96.0665 | 94.8944 |  |  |  |  | - | 92.5384 | (percent) | 85 | average
| CBOD | Effluent | maximum | (mg / l) | 19 | 15 | 13 | 14 | 12 | 13 | 11 | 11 |  |  |  |  | - | 19 |  |  | max
|  |  | average |  | 12.7143 | 11.6154 | 10.5 | 8.3846 | 8.8571 | 10.5833 | 8 | 8.7143 |  |  |  |  | - | 9.9211 | (mg / l) |  | average
|  |  | minimum |  | 8 | 8 | 8 | 6 | 5 | 8 | 6 | 6 |  |  |  |  | - | 5 |  |  | min
|  | Effluent | removal | (percent) | 93.9273 | 93.0378 | 92.293 | 93.5346 | 94.8318 | 95.8141 | 97.215 | 96.371 |  |  |  |  | - | 94.6281 | (percent) |  | average
TOTAL SUSPENDED SOLIDS
|  | Influent | maximum | (mg / l) | 254 | 224 | 182 | 182 | 274 | 352 | 360 | 354 |  |  |  |  | - | 360 |  |  | max
|  |  | average |  | 183.7143 | 165.0769 | 132.0833 | 131.0769 | 192.0714 | 282.5833 | 273.1429 | 258 |  |  |  |  | - | 202.2186 | (mg / l) |  | average
|  |  | minimum |  | 116 | 96 | 92 | 81 | 72 | 228 | 206 | 178 |  |  |  |  | - | 72 |  |  | min
|  | Influent | maximum | (pounds) | 5670.8497 | 7069.1174 | 5500.7971 | 6078.0919 | 7161.6914 | 7730.9298 | 6139.908 | 6955.7602 |  |  |  |  | - | 7730.9298 |  |  | max
|  |  | average |  | 3838.1788 | 4361.8957 | 4261.6955 | 4519.079 | 5643.2473 | 5758.1243 | 4795.6787 | 5285.42 |  |  |  |  | - | 4807.9149 | (pounds) |  | average
|  |  | minimum |  | 2326.1594 | 2787.0278 | 3428.7825 | 3726.9792 | 3704.9616 | 4816.5502 | 3709.165 | 4119.543 |  |  |  |  | - | 2326.1594 |  |  | min
|  | Primary | maximum | (mg / l) | 73 | 86 | 58 | 43 | 118 | 114 | 84 | 104 |  |  |  |  | - | - |  |  | max
|  |  | average |  | 67.75 | 65.6 | 44.6667 | 38 | 84.8 | 102.5 | 78.5 | 94 |  |  |  |  | - | 71.9771 | (mg / l) |  | average
|  |  | minimum |  | 64 | 44 | 25 | 34 | 50 | 82 | 71 | 71 |  |  |  |  | - | - |  |  | min
|  | Primary | maximum | (pounds) | 1631.6376 | 2430.0091 | 1693.02 | 1362.756 | 3025.1849 | 2588.9195 | 1449.1584 | 2438.5743 |  |  |  |  | - | - |  |  | max
|  |  | average |  | 1423.3878 | 1669.0158 | 1416.1876 | 1254.7322 | 2465.8828 | 2145.9988 | 1374.5967 | 1970.6232 |  |  |  |  | - | 1715.0531 | (pounds) |  | average
|  |  | minimum |  | 1307.712 | 1277.3878 | 994.545 | 1087.8696 | 2218.023 | 1613.2729 | 1219.2163 | 1565.6182 |  |  |  |  | - | - |  |  | min
|  | Effluent | maximum | (mg / l) | 29 | 28 | 21 | 23 | 27 | 30 | 19 | 27 |  |  |  |  | - | 30 |  | 50 | max
|  |  | average |  | 21.2143 | 20.6154 | 16.4167 | 13.6923 | 20.9286 | 22.3333 | 15.3571 | 19.2 |  |  |  |  | - | 18.7197 | (mg / l) | 30 | average
|  |  | minimum |  | 14 | 16 | 8 | 9 | 14 | 17 | 9 | 13 |  |  |  |  | - | 8 |  |  | min
|  | Effluent | maximum | (pounds) | 649.1522 | 808.0459 | 647.626 | 1368.0602 | 926.2404 | 702.8118 | 374.1241 | 603.6075 |  |  |  |  | - | 1368.0602 |  | 1605 | max
|  |  | average |  | 446.4211 | 552.72 | 532.9413 | 506.365 | 642.1586 | 460.2617 | 271.218 | 400.8596 |  |  |  |  | - | 476.6182 | (pounds) | 963 | average
|  |  | minimum |  | 246.7139 | 404.7235 | 278.4226 | 316.5947 | 462.3696 | 317.5872 | 170.3862 | 260.3164 |  |  |  |  | - | 170.3862 |  |  | min
|  | Effluent | removal | (percent) | 88.4526 | 87.5116 | 87.571 | 89.554 | 89.1038 | 92.0967 | 94.3776 | 92.5581 |  |  |  |  | - | 90.1532 | (percent) | 85 | average
BRUNSWICK SEWER DISTRICT |  |  |  |  | JUNE: State Discharge License Number W 002600-5L-C-R |  |  |  | Gregory H. Thulen
Annual Report of Treatment Operations: 2008. |  |  |  |  | JUNE: N.P.D.E.S. Permit Number ME 0100102 |  |  |  | Treatment Operations Division Supervisor
'file:///tmp/in/input.xls'#$ANNUAL 08 | [19 empty] | Page 3.
[17 empty] | A N N U A L |  |  | P E R M I T
| Parameter |  | Function | Units | JANUARY | FEBRUARY | MARCH | APRIL | MAY | JUNE | JULY | AUGUST | SEPTEMBER | OCTOBER | NOVEMBER | DECEMBER | Total | Max/Avg/Min | Units | Limits
SLUDGE DEWATERING
|  | Dewatered | total volume | (gallons) | JANUARY: 482819; FEBRUARY: 402698; MARCH: 379520; APRIL: 442802; MAY: 455356; JUNE: 536763; JULY: 553240 | 3253198 | - | (gallons) |  | total
|  |  | monthly average | (gallons) | JANUARY: 53646.5556; FEBRUARY: 50337.25; MARCH: 47440; APRIL: 44280.2; MAY: 35027.3846; JUNE: 48796.6364; JULY: 61471.1111 | - | 48714.1625 | (gallons / mo) |  | average
|  | Feed solids | monthly average | (percent) | JANUARY: 3.1111; FEBRUARY: 3.875; MARCH: 4; APRIL: 2.8; MAY: 3.6923; JUNE: 3.9091; JULY: 3.1111 | - | 3.4998 | (percent) |  | average
|  | Press run time | total | (hours) | JANUARY: 31.25; FEBRUARY: 30.75; MARCH: 24.5; APRIL: 31.75; MAY: 32.25; JUNE: 37; JULY: 33.5 | 221 | 4.25 | (hours / wk) |  | total; average
|  | Polymer | total added | (pounds) | JANUARY: 235.6; FEBRUARY: 189.1; MARCH: 186; APRIL: 235.6; MAY: 248; JUNE: 285.2; JULY: 269.7 | 1649.2 | 31.7154 | (pounds / wk) |  | total; average
|  | Cake solids | monthly average | (percent) | JANUARY: 32.2222; FEBRUARY: 32.25; MARCH: 32.25; APRIL: 28.3; MAY: 26.4615; JUNE: 27.8182; JULY: 32.3333 | - | 30.2336 | (percent) |  | average
|  | Generated | total volume | (cubic yards) | JANUARY: 185; FEBRUARY: 152; MARCH: 148; APRIL: 157; MAY: 205; JUNE: 278; JULY: 228 | 1353 | 26.0192 | (cu. yd. / wk) |  | total; average
|  | Lime | total added | (pounds) | JANUARY: 14415; FEBRUARY: 13102.5; MARCH: 9967.5; APRIL: 1995; JUNE: 9450; JULY: 16627.5 | 65557.5 | 1260.7212 | (pounds / wk) |  | total; average
|  | pH | monthly average | (std units) | JANUARY: 12.4033; FEBRUARY: 12.365; MARCH: 12.3757; APRIL: 12.28; JUNE: 12.348; JULY: 12.3544 | - | 12.3544 | (std units) | 12 | average